## All Systems
System | Page | Equipment | Type | Primary From | Alternate From | Properties
SYSTEM A | 1 | GENAA100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM A | 1 | GSBAA110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM A | 1 | TRNAA110 | TRN | - | - | -
SYSTEM A | 1 | GSBAB110 | GSB | - | - | -
SYSTEM A | 1 | MSBAA110 | MSB | TRNAA110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM A | 1 | MDPAA110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM A | 1 | UPSAA110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM A | 1 | UPSAA210 | UPS | MDPAA110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM A | 1 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 1 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 1 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 1 | TRNAA310 | TRN | - | - | 480V:208Y/120, 75KVA, NEMA 1
SYSTEM A | 1 | UPBAA110 | UPB | - | - | -
SYSTEM A | 1 | UPBAA210 | UPB | - | - | -
SYSTEM A | 1 | UPBAA310 | UPB | - | - | -
SYSTEM A | 1 | UPBAA410 | UPB | - | - | -
SYSTEM A | 1 | UPBAA510 | UPB | - | - | -
SYSTEM A | 1 | UPBAA120 | UPB | - | - | -
SYSTEM A | 1 | UPBAA220 | UPB | - | - | -
SYSTEM A | 1 | UPBAA320 | UPB | EPPAZ110 | - | -
SYSTEM A | 1 | UPBAA420 | UPB | EPPAZ110 | - | -
SYSTEM A | 1 | UPBAA520 | UPB | EPPAZ110 | - | -
SYSTEM A | 1 | EPPAZ210 | EPP | UPBAA520 | EPPAZ110, EPPAZ110, EPPAZ110 | -
SYSTEM A | 1 | EPPAZ210 | EPP | ELPAA110 | EPPAZ110, EPPAZ110, EPPAZ110 | -
SYSTEM A | 1 | ELPAA110 | ELP | TRNAA310 | EPPAZ110 | -
SYSTEM A | 1 | MBCAA110 | MBC | UPBAA110 | UPBAA210 | 2500AF, 2500AT
SYSTEM A | 1 | TRNAA210 | TRN | EPPAA230 | ELPAA110, TRNAA310 | -
SYSTEM A | 1 | EPPAA230 | EPP | ELPAA110 | TRNAA310 | -
SYSTEM A | 1 | EPPAA120 | EPP | TRNAA210 | EPPAA230 | -
SYSTEM A | 1 | EPPAA320 | EPP | EPPAA230 | TRNAA210 | -
SYSTEM A | 1 | STSAA110 | STS | - | - | -
SYSTEM A | 1 | STSAA210 | STS | - | - | -
SYSTEM A | 2 | MBCAA110 | MBC | - | - | -
SYSTEM A | 2 | MBCAA110 | MBC | - | - | -
SYSTEM A | 2 | BSWAZ110 | BSW | MBCAA110 | - | -
SYSTEM A | 2 | BSWAZ110 | BSW | MBCAA110 | - | -
SYSTEM A | 2 | STSAA110 | STS | BSWAZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 2 | STSAA210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 2 | UDPAA110 | UDP | STSAA110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 2 | UDPAA220 | UDP | STSAA210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 2 | PDUAA110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 2 | PDUAA310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 2 | PDUAA520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 2 | PDUAA720 | PDU | - | - | 500KVA, K4 RATING
SYSTEM A | 2 | TRNAA410 | TRN | - | - | -
SYSTEM A | 2 | RPPAA111 | RPP | - | - | -
SYSTEM A | 2 | RPPAA211 | RPP | TRNAA410 | - | -
SYSTEM A | 2 | RPPAA311 | RPP | TRNAA410 | - | -
SYSTEM A | 2 | RPPAA411 | RPP | TRNAA410 | - | -
SYSTEM A | 2 | RPPAA511 | RPP | TRNAA410 | - | -
SYSTEM A | 2 | RPPAA131 | RPP | TRNAA410 | - | -
SYSTEM A | 2 | RPPAA231 | RPP | TRNAA410 | - | -
SYSTEM A | 2 | RPPAA331 | RPP | - | - | -
SYSTEM A | 2 | RPPAA431 | RPP | - | - | -
SYSTEM A | 2 | RPPAA531 | RPP | - | - | -
SYSTEM A | 2 | RPPAA152 | RPP | - | - | -
SYSTEM A | 2 | RPPAA252 | RPP | - | - | -
SYSTEM A | 2 | RPPAA352 | RPP | - | - | -
SYSTEM A | 2 | RPPAA452 | RPP | - | - | -
SYSTEM A | 2 | RPPAA552 | RPP | - | - | -
SYSTEM A | 2 | RPPAA172 | RPP | - | - | -
SYSTEM A | 2 | RPPAA272 | RPP | - | - | -
SYSTEM A | 2 | RPPAA372 | RPP | - | - | -
SYSTEM A | 2 | RPPAA472 | RPP | - | - | -
SYSTEM A | 2 | RPPAA572 | RPP | RPPAA472 | RPPAA372, RPPAA272, RPPAA172 | -
SYSTEM A | 2 | RPPAA610 | RPP | RPPAA511 | RPPAA411, RPPAA311, RPPAA131, RPPAA211, RPPAA231, TRNAA410 | -
SYSTEM A | 2 | MBCAA110 | MBC | RPPAA531 | RPPAA431, RPPAA331, RPPAA231, RPPAA152 | -
SYSTEM A | 2 | UDPAA310 | UDP | MBCAA110 | RPPAA331, RPPAA431, RPPAA531, RPPAA152, RPPAA252, RPPAA352, RPPAA452, RPPAA552 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 2 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 2 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 2 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 2 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 2 | ATSAA130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
SYSTEM A | 2 | ATSAA230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM A | 2 | ATSAA330 | ATS | BSWAZ310 | BSWAZ310 | 800A,480V, 3, , 3-POLE
SYSTEM A | 2 | ATSAA430 | ATS | - | - | -
SYSTEM A | 2 | PDUAA210 | PDU | ATSAA130 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 2 | PDUAA420 | PDU | ATSAA230 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 2 | PDUAA630 | PDU | ATSAA330 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 2 | PDUAA840 | PDU | ATSAA430 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 2 | RPPAA121 | RPP | RPPAA421 | RPPAA521 | -
SYSTEM A | 2 | RPPAA221 | RPP | RPPAA421 | RPPAA521 | -
SYSTEM A | 2 | RPPAA321 | RPP | RPPAA421 | RPPAA521 | -
SYSTEM A | 2 | RPPAA421 | RPP | - | - | -
SYSTEM A | 2 | RPPAA521 | RPP | RPPAA141 | - | -
SYSTEM A | 2 | RPPAA141 | RPP | - | - | -
SYSTEM A | 2 | RPPAA241 | RPP | - | - | -
SYSTEM A | 2 | RPPAA341 | RPP | RPPAA441 | RPPAA241, RPPAA541, RPPAA141 | -
SYSTEM A | 2 | RPPAA441 | RPP | RPPAA241 | RPPAA141 | -
SYSTEM A | 2 | RPPAA541 | RPP | RPPAA241 | RPPAA141 | -
SYSTEM A | 2 | RPPAA162 | RPP | RPPAA462 | RPPAA562 | -
SYSTEM A | 2 | RPPAA262 | RPP | RPPAA462 | RPPAA562 | -
SYSTEM A | 2 | RPPAA362 | RPP | RPPAA462 | RPPAA562 | -
SYSTEM A | 2 | RPPAA462 | RPP | - | - | -
SYSTEM A | 2 | RPPAA562 | RPP | - | - | -
SYSTEM A | 2 | RPPAA182 | RPP | RPPAA382 | RPPAA482, RPPAA582 | -
SYSTEM A | 2 | RPPAA282 | RPP | RPPAA382 | RPPAA482, RPPAA582 | -
SYSTEM A | 2 | RPPAA382 | RPP | - | - | -
SYSTEM A | 2 | RPPAA482 | RPP | - | - | -
SYSTEM A | 2 | RPPAA582 | RPP | - | - | -
SYSTEM A | 3 | GENAB100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM A | 3 | GSBAB110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM A | 3 | TRNAB110 | TRN | - | - | -
SYSTEM A | 3 | GSBAA110 | GSB | - | - | -
SYSTEM A | 3 | GSBAC110 | GSB | - | - | -
SYSTEM A | 3 | MSBAB110 | MSB | TRNAB110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM A | 3 | MDPAB110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM A | 3 | UPSAB110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM A | 3 | UPSAB210 | UPS | MDPAB110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM A | 3 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 3 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 3 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 3 | TRNAB310 | TRN | - | - | -
SYSTEM A | 3 | TRNAB410 | TRN | TRNAB310 | - | 480V:480Y/277, 30KVA, NEMA 1
SYSTEM A | 3 | UPBAB110 | UPB | - | - | -
SYSTEM A | 3 | UPBAB210 | UPB | - | - | -
SYSTEM A | 3 | UPBAB310 | UPB | - | - | -
SYSTEM A | 3 | UPBAB410 | UPB | - | - | -
SYSTEM A | 3 | UPBAB510 | UPB | - | - | -
SYSTEM A | 3 | UPBAB120 | UPB | - | - | -
SYSTEM A | 3 | UPBAB220 | UPB | - | - | -
SYSTEM A | 3 | UPBAB320 | UPB | EPPAZ110 | - | -
SYSTEM A | 3 | UPBAB420 | UPB | EPPAZ110 | - | -
SYSTEM A | 3 | UPBAB520 | UPB | EPPAZ110 | - | -
SYSTEM A | 3 | EPPAZ210 | EPP | UPBAB520 | EPPAZ110, EPPAZ110, EPPAZ110 | -
SYSTEM A | 3 | EPPAZ210 | EPP | ELPAB110 | EPPAZ110, EPPAZ110, EPPAZ110 | -
SYSTEM A | 3 | ELPAB110 | ELP | TRNAB310 | TRNAB410, EPPAZ110 | -
SYSTEM A | 3 | EPPAB230 | EPP | ELPAB110 | TRNAB410, TRNAB310 | -
SYSTEM A | 3 | MBCAB110 | MBC | UPBAB110 | UPBAB210 | 2500AF, 2500AT
SYSTEM A | 3 | TRNAB210 | TRN | EPPAB230 | ELPAB110, TRNAB410, TRNAB310 | -
SYSTEM A | 3 | ELPAB240 | ELP | TRNAB210 | EPPAB230, ELPAB110, TRNAB410 | -
SYSTEM A | 3 | EPPAB120 | EPP | TRNAB210 | ELPAB240, EPPAB230 | -
SYSTEM A | 3 | STSAB110 | STS | - | - | -
SYSTEM A | 3 | STSAB210 | STS | - | - | -
SYSTEM A | 4 | MBCAB110 | MBC | - | - | -
SYSTEM A | 4 | MBCAB110 | MBC | - | - | -
SYSTEM A | 4 | BSWAZ110 | BSW | MBCAB110 | - | -
SYSTEM A | 4 | BSWAZ110 | BSW | MBCAB110 | - | -
SYSTEM A | 4 | BSWAZ110 | BSW | - | - | -
SYSTEM A | 4 | STSAB110 | STS | BSWAZ110 | - | 1600A, 480V, 3, 3 POLE, 65kAIC, , 3W
SYSTEM A | 4 | STSAB210 | STS | - | - | 1600A, 480V, 3, 3 POLE, 65kAIC, , 3W
SYSTEM A | 4 | UDPAB110 | UDP | STSAB110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 4 | UDPAB220 | UDP | STSAB210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 4 | PDUAB110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 4 | PDUAB310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 4 | PDUAB520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 4 | PDUAB720 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 4 | TRNAB550 | TRN | - | - | 415V:208Y/120, 30KVA, NEMA 1
SYSTEM A | 4 | RPPAB111 | RPP | - | - | -
SYSTEM A | 4 | RPPAB211 | RPP | - | - | -
SYSTEM A | 4 | RPPAB311 | RPP | - | - | -
SYSTEM A | 4 | RPPAB411 | RPP | - | - | -
SYSTEM A | 4 | RPPAB511 | RPP | - | - | -
SYSTEM A | 4 | RPPAB131 | RPP | - | - | -
SYSTEM A | 4 | RPPAB231 | RPP | - | - | -
SYSTEM A | 4 | RPPAB331 | RPP | - | - | -
SYSTEM A | 4 | RPPAB431 | RPP | - | - | -
SYSTEM A | 4 | RPPAB531 | RPP | - | - | -
SYSTEM A | 4 | RPPAB152 | RPP | - | - | -
SYSTEM A | 4 | RPPAB252 | RPP | TRNAB550 | - | -
SYSTEM A | 4 | RPPAB352 | RPP | TRNAB550 | - | -
SYSTEM A | 4 | RPPAB452 | RPP | TRNAB550 | - | -
SYSTEM A | 4 | RPPAB552 | RPP | TRNAB550 | - | -
SYSTEM A | 4 | RPPAB172 | RPP | TRNAB550 | - | -
SYSTEM A | 4 | RPPAB272 | RPP | - | - | -
SYSTEM A | 4 | RPPAB372 | RPP | - | - | -
SYSTEM A | 4 | RPPAB472 | RPP | - | - | -
SYSTEM A | 4 | RPPAB572 | RPP | - | - | -
SYSTEM A | 4 | RPPAB650 | RPP | RPPAB552 | RPPAB452, RPPAB352, RPPAB172, RPPAB252, TRNAB550 | -
SYSTEM A | 4 | MBCAB110 | MBC | RPPAB531 | RPPAB431, RPPAB331, RPPAB231, RPPAB152 | -
SYSTEM A | 4 | UDPAB310 | UDP | MBCAB110 | RPPAB331, RPPAB431, RPPAB531, RPPAB152, RPPAB252, RPPAB352, RPPAB452, RPPAB552 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 4 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 4 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 4 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 4 | BSWAZ210 | BSW | BSWAZ310 | - | -
SYSTEM A | 4 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 4 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 4 | ATSAB130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
SYSTEM A | 4 | ATSAB230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM A | 4 | ATSAB330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
SYSTEM A | 4 | ATSAB430 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM A | 4 | PDUAB210 | PDU | ATSAB130 | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 4 | PDUAB420 | PDU | ATSAB230 | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 4 | PDUAB630 | PDU | ATSAB330 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 4 | PDUAB840 | PDU | ATSAB430 | - | 500KVA, K4 RATING
SYSTEM A | 4 | RPPAB121 | RPP | - | - | -
SYSTEM A | 4 | RPPAB221 | RPP | - | - | -
SYSTEM A | 4 | RPPAB321 | RPP | - | - | -
SYSTEM A | 4 | RPPAB421 | RPP | - | - | -
SYSTEM A | 4 | RPPAB521 | RPP | - | - | -
SYSTEM A | 4 | RPPAB141 | RPP | - | - | -
SYSTEM A | 4 | RPPAB241 | RPP | - | - | -
SYSTEM A | 4 | RPPAB341 | RPP | - | - | -
SYSTEM A | 4 | RPPAB441 | RPP | - | - | -
SYSTEM A | 4 | RPPAB541 | RPP | - | - | -
SYSTEM A | 4 | RPPAB162 | RPP | - | - | -
SYSTEM A | 4 | RPPAB262 | RPP | - | - | -
SYSTEM A | 4 | RPPAB362 | RPP | - | - | -
SYSTEM A | 4 | RPPAB462 | RPP | - | - | -
SYSTEM A | 4 | RPPAB562 | RPP | - | - | -
SYSTEM A | 4 | RPPAB182 | RPP | - | - | -
SYSTEM A | 4 | RPPAB282 | RPP | - | - | -
SYSTEM A | 4 | RPPAB382 | RPP | - | - | -
SYSTEM A | 4 | RPPAB482 | RPP | - | - | -
SYSTEM A | 4 | RPPAB582 | RPP | - | - | -
SYSTEM A | 5 | GENAC100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM A | 5 | GSBAC110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM A | 5 | TRNAC110 | TRN | - | - | -
SYSTEM A | 5 | GSBAB110 | GSB | - | - | -
SYSTEM A | 5 | GSBAZ110 | GSB | - | - | -
SYSTEM A | 5 | MSBAC110 | MSB | TRNAC110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM A | 5 | MDPAC110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM A | 5 | UPSAC110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM A | 5 | UPSAC210 | UPS | MDPAC110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM A | 5 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 5 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 5 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 5 | TRNAC310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
SYSTEM A | 5 | UPBAC110 | UPB | - | - | -
SYSTEM A | 5 | UPBAC210 | UPB | - | - | -
SYSTEM A | 5 | UPBAC310 | UPB | - | - | -
SYSTEM A | 5 | UPBAC410 | UPB | - | - | -
SYSTEM A | 5 | UPBAC510 | UPB | - | - | -
SYSTEM A | 5 | UPBAC120 | UPB | - | - | -
SYSTEM A | 5 | UPBAC220 | UPB | - | - | -
SYSTEM A | 5 | UPBAC320 | UPB | EPPAZ110 | - | -
SYSTEM A | 5 | UPBAC420 | UPB | EPPAZ110 | - | -
SYSTEM A | 5 | UPBAC520 | UPB | EPPAZ110 | - | -
SYSTEM A | 5 | EPPAZ210 | EPP | UPBAC520 | EPPAZ110, EPPAZ110, EPPAZ110 | -
SYSTEM A | 5 | EPPAZ210 | EPP | EPPAZ110 | EPPAZ110, EPPAZ110 | -
SYSTEM A | 5 | EPPAZ210 | EPP | ELPAC110 | EPPAZ110, EPPAZ110, EPPAZ110 | -
SYSTEM A | 5 | ELPAC110 | ELP | TRNAC310 | EPPAZ110 | -
SYSTEM A | 5 | MBCAC110 | MBC | UPBAC110 | UPBAC210 | 2500AF, 2500AT
SYSTEM A | 5 | TRNAC210 | TRN | ELPAC110 | EPPAZ210, TRNAC310 | -
SYSTEM A | 5 | ELPAC230 | ELP | TRNAC210 | ELPAC110, TRNAC310 | -
SYSTEM A | 5 | EPPAC120 | EPP | TRNAC210 | ELPAC230 | -
SYSTEM A | 5 | STSAC110 | STS | - | - | -
SYSTEM A | 5 | STSAC210 | STS | - | - | -
SYSTEM A | 6 | MBCAC110 | MBC | - | - | -
SYSTEM A | 6 | MBCAC110 | MBC | - | - | -
SYSTEM A | 6 | BSWAZ110 | BSW | MBCAC110 | - | -
SYSTEM A | 6 | BSWAZ110 | BSW | MBCAC110 | - | -
SYSTEM A | 6 | BSWAZ110 | BSW | - | - | -
SYSTEM A | 6 | STSAC110 | STS | BSWAZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 6 | STSAC210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 6 | UDPAC110 | UDP | STSAC110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 6 | UDPAC220 | UDP | STSAC210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 6 | PDUAC110 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
SYSTEM A | 6 | PDUAC310 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
SYSTEM A | 6 | PDUAC520 | PDU | - | - | 500KVA, 480V:415Y/240V
SYSTEM A | 6 | PDUAC720 | PDU | - | - | 500KVA
SYSTEM A | 6 | RPPAC111 | RPP | - | - | -
SYSTEM A | 6 | RPPAC211 | RPP | - | - | -
SYSTEM A | 6 | RPPAC311 | RPP | - | - | -
SYSTEM A | 6 | RPPAC411 | RPP | - | - | -
SYSTEM A | 6 | RPPAC511 | RPP | - | - | -
SYSTEM A | 6 | RPPAC131 | RPP | - | - | -
SYSTEM A | 6 | RPPAC231 | RPP | - | - | -
SYSTEM A | 6 | RPPAC331 | RPP | - | - | -
SYSTEM A | 6 | RPPAC431 | RPP | - | - | -
SYSTEM A | 6 | RPPAC531 | RPP | - | - | -
SYSTEM A | 6 | RPPAC152 | RPP | - | - | -
SYSTEM A | 6 | RPPAC252 | RPP | - | - | -
SYSTEM A | 6 | RPPAC352 | RPP | - | - | -
SYSTEM A | 6 | RPPAC452 | RPP | - | - | -
SYSTEM A | 6 | RPPAC552 | RPP | - | - | -
SYSTEM A | 6 | RPPAC172 | RPP | - | - | -
SYSTEM A | 6 | RPPAC272 | RPP | - | - | -
SYSTEM A | 6 | RPPAC372 | RPP | - | - | -
SYSTEM A | 6 | RPPAC472 | RPP | - | - | -
SYSTEM A | 6 | RPPAC572 | RPP | - | - | -
SYSTEM A | 6 | MBCAC110 | MBC | RPPAC531 | RPPAC431, RPPAC331, RPPAC231, RPPAC152 | -
SYSTEM A | 6 | UDPAC310 | UDP | MBCAC110 | RPPAC331, RPPAC431, RPPAC531, RPPAC152, RPPAC252, RPPAC352, RPPAC452, RPPAC552 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 6 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 6 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 6 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 6 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 6 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 6 | ATSAC130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
SYSTEM A | 6 | ATSAC230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM A | 6 | ATSAC330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
SYSTEM A | 6 | ATSAC430 | ATS | - | - | -
SYSTEM A | 6 | PDUAC210 | PDU | ATSAC130 | - | 500KVA, 480V:415Y/240V
SYSTEM A | 6 | PDUAC420 | PDU | ATSAC230 | - | 500KVA, 480V:415Y/240V
SYSTEM A | 6 | PDUAC630 | PDU | ATSAC330 | - | 500KVA, 480V:415Y/240V
SYSTEM A | 6 | PDUAC840 | PDU | ATSAC430 | - | 500KVA, 480V:415Y/240V
SYSTEM A | 6 | RPPAC121 | RPP | - | - | -
SYSTEM A | 6 | RPPAC221 | RPP | - | - | -
SYSTEM A | 6 | RPPAC321 | RPP | - | - | -
SYSTEM A | 6 | RPPAC421 | RPP | - | - | -
SYSTEM A | 6 | RPPAC521 | RPP | - | - | -
SYSTEM A | 6 | RPPAC141 | RPP | - | - | -
SYSTEM A | 6 | RPPAC241 | RPP | - | - | -
SYSTEM A | 6 | RPPAC341 | RPP | - | - | -
SYSTEM A | 6 | RPPAC441 | RPP | - | - | -
SYSTEM A | 6 | RPPAC541 | RPP | - | - | -
SYSTEM A | 6 | RPPAC162 | RPP | - | - | -
SYSTEM A | 6 | RPPAC262 | RPP | - | - | -
SYSTEM A | 6 | RPPAC362 | RPP | - | - | -
SYSTEM A | 6 | RPPAC462 | RPP | - | - | -
SYSTEM A | 6 | RPPAC562 | RPP | - | - | -
SYSTEM A | 6 | RPPAC182 | RPP | - | - | -
SYSTEM A | 6 | RPPAC282 | RPP | - | - | -
SYSTEM A | 6 | RPPAC382 | RPP | - | - | -
SYSTEM A | 6 | RPPAC482 | RPP | - | - | -
SYSTEM A | 6 | RPPAC582 | RPP | - | - | -
SYSTEM A | 7 | GENAD100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM A | 7 | GSBAD110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM A | 7 | TRNAD110 | TRN | - | - | -
SYSTEM A | 7 | GSBAZ110 | GSB | - | - | -
SYSTEM A | 7 | GSBAE110 | GSB | - | - | -
SYSTEM A | 7 | MSBAD110 | MSB | TRNAD110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM A | 7 | MDPAD110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM A | 7 | UPSAD110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM A | 7 | UPSAD210 | UPS | MDPAD110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM A | 7 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 7 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 7 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 7 | TRNAD310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
SYSTEM A | 7 | UPBAD110 | UPB | - | - | -
SYSTEM A | 7 | UPBAD210 | UPB | - | - | -
SYSTEM A | 7 | UPBAD310 | UPB | - | - | -
SYSTEM A | 7 | UPBAD410 | UPB | - | - | -
SYSTEM A | 7 | UPBAD510 | UPB | - | - | -
SYSTEM A | 7 | UPBAD120 | UPB | - | - | -
SYSTEM A | 7 | UPBAD220 | UPB | - | - | -
SYSTEM A | 7 | UPBAD320 | UPB | EPPAZ110 | - | -
SYSTEM A | 7 | UPBAD420 | UPB | EPPAZ110 | - | -
SYSTEM A | 7 | UPBAD520 | UPB | EPPAZ110 | - | -
SYSTEM A | 7 | EPPAZ210 | EPP | UPBAD520 | EPPAZ110, EPPAZ110, EPPAZ110 | -
SYSTEM A | 7 | EPPAZ210 | EPP | EPPAZ110 | EPPAZ110, EPPAZ110 | -
SYSTEM A | 7 | EPPAZ210 | EPP | ELPAD110 | EPPAZ110, EPPAZ110, EPPAZ110 | -
SYSTEM A | 7 | ELPAD110 | ELP | TRNAD310 | EPPAZ110 | -
SYSTEM A | 7 | MBCAD110 | MBC | UPBAD110 | UPBAD210 | 2500AF, 2500AT
SYSTEM A | 7 | TRNAD210 | TRN | ELPAD110 | EPPAZ210, TRNAD310 | -
SYSTEM A | 7 | ELPAD230 | ELP | TRNAD210 | ELPAD110, TRNAD310 | -
SYSTEM A | 7 | EPPAD120 | EPP | TRNAD210 | ELPAD230 | -
SYSTEM A | 7 | STSAD110 | STS | - | - | -
SYSTEM A | 7 | STSAD210 | STS | - | - | -
SYSTEM A | 8 | MBCAD110 | MBC | - | - | -
SYSTEM A | 8 | MBCAD110 | MBC | - | - | -
SYSTEM A | 8 | BSWAZ110 | BSW | MBCAD110 | - | -
SYSTEM A | 8 | BSWAZ110 | BSW | MBCAD110 | - | -
SYSTEM A | 8 | BSWAZ110 | BSW | - | - | -
SYSTEM A | 8 | STSAD110 | STS | BSWAZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 8 | STSAD210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 8 | UDPAD110 | UDP | STSAD110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 8 | UDPAD220 | UDP | STSAD210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 8 | PDUAD110 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
SYSTEM A | 8 | PDUAD310 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
SYSTEM A | 8 | PDUAD520 | PDU | - | - | 500KVA, 480V:415Y/240V
SYSTEM A | 8 | PDUAD720 | PDU | - | - | 500KVA
SYSTEM A | 8 | RPPAD111 | RPP | - | - | -
SYSTEM A | 8 | RPPAD211 | RPP | - | - | -
SYSTEM A | 8 | RPPAD311 | RPP | - | - | -
SYSTEM A | 8 | RPPAD411 | RPP | - | - | -
SYSTEM A | 8 | RPPAD511 | RPP | - | - | -
SYSTEM A | 8 | RPPAD131 | RPP | - | - | -
SYSTEM A | 8 | RPPAD231 | RPP | - | - | -
SYSTEM A | 8 | RPPAD331 | RPP | - | - | -
SYSTEM A | 8 | RPPAD431 | RPP | - | - | -
SYSTEM A | 8 | RPPAD531 | RPP | - | - | -
SYSTEM A | 8 | RPPAD152 | RPP | - | - | -
SYSTEM A | 8 | RPPAD252 | RPP | - | - | -
SYSTEM A | 8 | RPPAD352 | RPP | - | - | -
SYSTEM A | 8 | RPPAD452 | RPP | - | - | -
SYSTEM A | 8 | RPPAD552 | RPP | - | - | -
SYSTEM A | 8 | RPPAD172 | RPP | - | - | -
SYSTEM A | 8 | RPPAD272 | RPP | - | - | -
SYSTEM A | 8 | RPPAD372 | RPP | - | - | -
SYSTEM A | 8 | RPPAD472 | RPP | - | - | -
SYSTEM A | 8 | RPPAD572 | RPP | - | - | -
SYSTEM A | 8 | MBCAD110 | MBC | RPPAD531 | RPPAD431, RPPAD331, RPPAD231, RPPAD152 | -
SYSTEM A | 8 | UDPAD310 | UDP | MBCAD110 | RPPAD331, RPPAD431, RPPAD531, RPPAD152, RPPAD252, RPPAD352, RPPAD452, RPPAD552 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 8 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 8 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 8 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 8 | BSWAZ210 | BSW | BSWAZ310 | - | -
SYSTEM A | 8 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 8 | ATSAD130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
SYSTEM A | 8 | ATSAD230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM A | 8 | ATSAD330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
SYSTEM A | 8 | ATSAD430 | ATS | - | - | -
SYSTEM A | 8 | PDUAD210 | PDU | ATSAD130 | - | 500KVA, 480V:415Y/240V
SYSTEM A | 8 | PDUAD420 | PDU | ATSAD230 | - | 500KVA, 480V:415Y/240V
SYSTEM A | 8 | PDUAD630 | PDU | ATSAD330 | - | 500KVA, 480V:415Y/240V
SYSTEM A | 8 | PDUAD840 | PDU | ATSAD430 | - | 500KVA, 480V:415Y/240V
SYSTEM A | 8 | RPPAD121 | RPP | - | - | -
SYSTEM A | 8 | RPPAD221 | RPP | - | - | -
SYSTEM A | 8 | RPPAD321 | RPP | - | - | -
SYSTEM A | 8 | RPPAD421 | RPP | - | - | -
SYSTEM A | 8 | RPPAD521 | RPP | - | - | -
SYSTEM A | 8 | RPPAD141 | RPP | - | - | -
SYSTEM A | 8 | RPPAD241 | RPP | - | - | -
SYSTEM A | 8 | RPPAD341 | RPP | - | - | -
SYSTEM A | 8 | RPPAD441 | RPP | - | - | -
SYSTEM A | 8 | RPPAD541 | RPP | - | - | -
SYSTEM A | 8 | RPPAD162 | RPP | - | - | -
SYSTEM A | 8 | RPPAD262 | RPP | - | - | -
SYSTEM A | 8 | RPPAD362 | RPP | - | - | -
SYSTEM A | 8 | RPPAD462 | RPP | - | - | -
SYSTEM A | 8 | RPPAD562 | RPP | - | - | -
SYSTEM A | 8 | RPPAD182 | RPP | - | - | -
SYSTEM A | 8 | RPPAD282 | RPP | - | - | -
SYSTEM A | 8 | RPPAD382 | RPP | - | - | -
SYSTEM A | 8 | RPPAD482 | RPP | - | - | -
SYSTEM A | 8 | RPPAD582 | RPP | - | - | -
SYSTEM A | 9 | GENAE100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM A | 9 | GSBAE110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM A | 9 | TRNAE110 | TRN | - | - | -
SYSTEM A | 9 | GSBAD110 | GSB | - | - | -
SYSTEM A | 9 | GSBAF110 | GSB | - | - | -
SYSTEM A | 9 | MSBAE110 | MSB | TRNAE110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM A | 9 | MDPAE110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM A | 9 | UPSAE110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM A | 9 | UPSAE210 | UPS | MDPAE110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM A | 9 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 9 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 9 | TRNAE310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
SYSTEM A | 9 | UPBAE110 | UPB | - | - | -
SYSTEM A | 9 | UPBAE210 | UPB | - | - | -
SYSTEM A | 9 | UPBAE310 | UPB | - | - | -
SYSTEM A | 9 | UPBAE410 | UPB | - | - | -
SYSTEM A | 9 | UPBAE510 | UPB | - | - | -
SYSTEM A | 9 | UPBAE120 | UPB | - | - | -
SYSTEM A | 9 | UPBAE220 | UPB | - | - | -
SYSTEM A | 9 | UPBAE320 | UPB | EPPAZ110 | - | -
SYSTEM A | 9 | UPBAE420 | UPB | EPPAZ110 | - | -
SYSTEM A | 9 | UPBAE520 | UPB | EPPAZ110 | - | -
SYSTEM A | 9 | EPPAZ210 | EPP | UPBAE520 | EPPAZ110, EPPAZ110 | -
SYSTEM A | 9 | EPPAZ210 | EPP | ELPAE110 | EPPAZ110, EPPAZ110 | -
SYSTEM A | 9 | EPPAZ210 | EPP | ELPAE110 | EPPAZ110, EPPAZ110 | -
SYSTEM A | 9 | ELPAE110 | ELP | TRNAE310 | - | -
SYSTEM A | 9 | MBCAE110 | MBC | UPBAE110 | UPBAE210 | 2500AF, 2500AT
SYSTEM A | 9 | TRNAE210 | TRN | ELPAE110 | EPPAZ210, TRNAE310 | -
SYSTEM A | 9 | ELPAE230 | ELP | TRNAE210 | ELPAE110, TRNAE310 | -
SYSTEM A | 9 | EPPAE120 | EPP | TRNAE210 | ELPAE230 | -
SYSTEM A | 9 | STSAE110 | STS | - | - | -
SYSTEM A | 9 | STSAE210 | STS | - | - | -
SYSTEM A | 10 | MBCAE110 | MBC | - | - | -
SYSTEM A | 10 | MBCAE110 | MBC | - | - | -
SYSTEM A | 10 | BSWAZ110 | BSW | MBCAE110 | - | -
SYSTEM A | 10 | BSWAZ110 | BSW | MBCAE110 | - | -
SYSTEM A | 10 | BSWAZ110 | BSW | - | - | -
SYSTEM A | 10 | STSAE110 | STS | BSWAZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 10 | STSAE210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 10 | UDPAE110 | UDP | STSAE110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 10 | UDPAE220 | UDP | STSAE210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 10 | PDUAE110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 10 | PDUAE310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 10 | PDUAE520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 10 | PDUAE720 | PDU | - | - | 500KVA, K4 RATING
SYSTEM A | 10 | TRNAE450 | TRN | - | - | -
SYSTEM A | 10 | RPPAE111 | RPP | - | - | -
SYSTEM A | 10 | RPPAE211 | RPP | - | - | -
SYSTEM A | 10 | RPPAE311 | RPP | - | - | -
SYSTEM A | 10 | RPPAE411 | RPP | - | - | -
SYSTEM A | 10 | RPPAE511 | RPP | - | - | -
SYSTEM A | 10 | RPPAE131 | RPP | - | - | -
SYSTEM A | 10 | RPPAE231 | RPP | - | - | -
SYSTEM A | 10 | RPPAE331 | RPP | - | - | -
SYSTEM A | 10 | RPPAE431 | RPP | - | - | -
SYSTEM A | 10 | RPPAE531 | RPP | - | - | -
SYSTEM A | 10 | RPPAE152 | RPP | - | - | -
SYSTEM A | 10 | RPPAE252 | RPP | TRNAE450 | - | -
SYSTEM A | 10 | RPPAE352 | RPP | TRNAE450 | - | -
SYSTEM A | 10 | RPPAE452 | RPP | TRNAE450 | - | -
SYSTEM A | 10 | RPPAE552 | RPP | TRNAE450 | - | -
SYSTEM A | 10 | RPPAE172 | RPP | TRNAE450 | - | -
SYSTEM A | 10 | RPPAE272 | RPP | - | - | -
SYSTEM A | 10 | RPPAE372 | RPP | - | - | -
SYSTEM A | 10 | RPPAE472 | RPP | - | - | -
SYSTEM A | 10 | RPPAE572 | RPP | - | - | -
SYSTEM A | 10 | RPPAE650 | RPP | RPPAE552 | RPPAE452, RPPAE352, RPPAE172, RPPAE252, TRNAE450 | -
SYSTEM A | 10 | MBCAE110 | MBC | RPPAE531 | RPPAE431, RPPAE331, RPPAE231, RPPAE152 | -
SYSTEM A | 10 | UDPAE310 | UDP | MBCAE110 | RPPAE331, RPPAE431, RPPAE531, RPPAE152, RPPAE252, RPPAE352, RPPAE452, RPPAE552 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 10 | RPPAE760 | RPP | RPPAE650 | - | -
SYSTEM A | 10 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 10 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 10 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 10 | BSWAZ210 | BSW | BSWAZ310 | - | -
SYSTEM A | 10 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 10 | ATSAE130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
SYSTEM A | 10 | ATSAE230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM A | 10 | ATSAE330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
SYSTEM A | 10 | ATSAE430 | ATS | - | - | -
SYSTEM A | 10 | PDUAE210 | PDU | ATSAE130 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 10 | PDUAE420 | PDU | ATSAE230 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 10 | PDUAE630 | PDU | ATSAE330 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 10 | PDUAE840 | PDU | ATSAE430 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 10 | RPPAE121 | RPP | - | - | -
SYSTEM A | 10 | RPPAE221 | RPP | - | - | -
SYSTEM A | 10 | RPPAE321 | RPP | - | - | -
SYSTEM A | 10 | RPPAE421 | RPP | - | - | -
SYSTEM A | 10 | RPPAE521 | RPP | - | - | -
SYSTEM A | 10 | RPPAE141 | RPP | - | - | -
SYSTEM A | 10 | RPPAE241 | RPP | - | - | -
SYSTEM A | 10 | RPPAE341 | RPP | - | - | -
SYSTEM A | 10 | RPPAE441 | RPP | - | - | -
SYSTEM A | 10 | RPPAE541 | RPP | - | - | -
SYSTEM A | 10 | RPPAE162 | RPP | - | - | -
SYSTEM A | 10 | RPPAE262 | RPP | - | - | -
SYSTEM A | 10 | RPPAE362 | RPP | - | - | -
SYSTEM A | 10 | RPPAE462 | RPP | - | - | -
SYSTEM A | 10 | RPPAE562 | RPP | - | - | -
SYSTEM A | 10 | RPPAE182 | RPP | - | - | -
SYSTEM A | 10 | RPPAE282 | RPP | - | - | -
SYSTEM A | 10 | RPPAE382 | RPP | - | - | -
SYSTEM A | 10 | RPPAE482 | RPP | - | - | -
SYSTEM A | 10 | RPPAE582 | RPP | - | - | -
SYSTEM A | 11 | GENAF100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM A | 11 | GSBAF110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM A | 11 | TRNAF110 | TRN | - | - | -
SYSTEM A | 11 | GSBAE110 | GSB | - | - | -
SYSTEM A | 11 | MSBAF110 | MSB | TRNAF110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM A | 11 | MDPAF110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM A | 11 | UPSAF110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM A | 11 | UPSAF210 | UPS | MDPAF110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM A | 11 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 11 | EPPAZ110 | EPP | - | - | -
SYSTEM A | 11 | TRNAF310 | TRN | - | - | 480V:208Y/120, 75KVA, NEMA 1
SYSTEM A | 11 | UPBAF110 | UPB | - | - | -
SYSTEM A | 11 | UPBAF210 | UPB | - | - | -
SYSTEM A | 11 | UPBAF310 | UPB | - | - | -
SYSTEM A | 11 | UPBAF410 | UPB | - | - | -
SYSTEM A | 11 | UPBAF510 | UPB | - | - | -
SYSTEM A | 11 | UPBAF120 | UPB | - | - | -
SYSTEM A | 11 | UPBAF220 | UPB | - | - | -
SYSTEM A | 11 | UPBAF320 | UPB | EPPAZ110 | - | -
SYSTEM A | 11 | UPBAF420 | UPB | EPPAZ110 | - | -
SYSTEM A | 11 | UPBAF520 | UPB | EPPAZ110 | - | -
SYSTEM A | 11 | EPPAZ210 | EPP | UPBAF520 | EPPAZ110, EPPAZ110 | -
SYSTEM A | 11 | EPPAZ210 | EPP | ELPAF110 | EPPAZ110, EPPAZ110 | -
SYSTEM A | 11 | EPPAZ210 | EPP | ELPAF110 | EPPAZ110, EPPAZ110 | -
SYSTEM A | 11 | ELPAF110 | ELP | TRNAF310 | - | -
SYSTEM A | 11 | MBCAF110 | MBC | UPBAF110 | UPBAF210 | 2500AF, 2500AT
SYSTEM A | 11 | TRNAF210 | TRN | EPPAF230 | EPPAZ210, ELPAF110, TRNAF310 | -
SYSTEM A | 11 | EPPAF230 | EPP | ELPAF110 | TRNAF310 | -
SYSTEM A | 11 | EPPAF120 | EPP | TRNAF210 | EPPAF230 | -
SYSTEM A | 11 | EPPAF320 | EPP | EPPAF230 | TRNAF210 | -
SYSTEM A | 11 | STSAF110 | STS | - | - | -
SYSTEM A | 11 | STSAF210 | STS | - | - | -
SYSTEM A | 12 | MBCAF110 | MBC | - | - | -
SYSTEM A | 12 | MBCAF110 | MBC | - | - | -
SYSTEM A | 12 | BSWAZ110 | BSW | MBCAF110 | - | -
SYSTEM A | 12 | BSWAZ110 | BSW | - | - | -
SYSTEM A | 12 | STSAF110 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 12 | STSAF210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM A | 12 | UDPAF110 | UDP | STSAF110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 12 | UDPAF220 | UDP | STSAF210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 12 | PDUAF110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 12 | PDUAF310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM A | 12 | PDUAF520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 12 | PDUAF720 | PDU | - | - | 500KVA, K4 RATING
SYSTEM A | 12 | TRNAF410 | TRN | - | - | -
SYSTEM A | 12 | RPPAF111 | RPP | - | - | -
SYSTEM A | 12 | RPPAF211 | RPP | TRNAF410 | - | -
SYSTEM A | 12 | RPPAF311 | RPP | TRNAF410 | - | -
SYSTEM A | 12 | RPPAF411 | RPP | TRNAF410 | - | -
SYSTEM A | 12 | RPPAF511 | RPP | TRNAF410 | - | -
SYSTEM A | 12 | RPPAF131 | RPP | TRNAF410 | - | -
SYSTEM A | 12 | RPPAF231 | RPP | TRNAF410 | - | -
SYSTEM A | 12 | RPPAF331 | RPP | - | - | -
SYSTEM A | 12 | RPPAF431 | RPP | - | - | -
SYSTEM A | 12 | RPPAF531 | RPP | - | - | -
SYSTEM A | 12 | RPPAF152 | RPP | - | - | -
SYSTEM A | 12 | RPPAF252 | RPP | - | - | -
SYSTEM A | 12 | RPPAF352 | RPP | - | - | -
SYSTEM A | 12 | RPPAF452 | RPP | - | - | -
SYSTEM A | 12 | RPPAF552 | RPP | - | - | -
SYSTEM A | 12 | RPPAF172 | RPP | - | - | -
SYSTEM A | 12 | RPPAF272 | RPP | - | - | -
SYSTEM A | 12 | RPPAF372 | RPP | - | - | -
SYSTEM A | 12 | RPPAF472 | RPP | - | - | -
SYSTEM A | 12 | RPPAF572 | RPP | - | - | -
SYSTEM A | 12 | RPPAF610 | RPP | RPPAF511 | RPPAF411, RPPAF311, RPPAF131, RPPAF211, RPPAF231, TRNAF410 | -
SYSTEM A | 12 | MBCAF110 | MBC | RPPAF531 | RPPAF431, RPPAF331, RPPAF231, RPPAF152 | -
SYSTEM A | 12 | UDPAF310 | UDP | MBCAF110 | RPPAF331, RPPAF431, RPPAF531, RPPAF152, RPPAF252, RPPAF352, RPPAF452, RPPAF552 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 12 | RPPAF760 | RPP | RPPAF610 | - | -
SYSTEM A | 12 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 12 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 12 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 12 | BSWAZ210 | BSW | - | - | -
SYSTEM A | 12 | BSWAZ310 | BSW | - | - | -
SYSTEM A | 12 | ATSAF130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
SYSTEM A | 12 | ATSAF230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM A | 12 | ATSAF330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
SYSTEM A | 12 | ATSAF430 | ATS | - | - | -
SYSTEM A | 12 | PDUAF210 | PDU | ATSAF130 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 12 | PDUAF420 | PDU | ATSAF230 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 12 | PDUAF630 | PDU | ATSAF330 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 12 | PDUAF840 | PDU | ATSAF430 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM A | 12 | RPPAF121 | RPP | - | - | -
SYSTEM A | 12 | RPPAF221 | RPP | - | - | -
SYSTEM A | 12 | RPPAF321 | RPP | - | - | -
SYSTEM A | 12 | RPPAF421 | RPP | - | - | -
SYSTEM A | 12 | RPPAF521 | RPP | - | - | -
SYSTEM A | 12 | RPPAF141 | RPP | - | - | -
SYSTEM A | 12 | RPPAF241 | RPP | - | - | -
SYSTEM A | 12 | RPPAF341 | RPP | - | - | -
SYSTEM A | 12 | RPPAF441 | RPP | - | - | -
SYSTEM A | 12 | RPPAF541 | RPP | - | - | -
SYSTEM A | 12 | RPPAF162 | RPP | - | - | -
SYSTEM A | 12 | RPPAF262 | RPP | - | - | -
SYSTEM A | 12 | RPPAF362 | RPP | - | - | -
SYSTEM A | 12 | RPPAF462 | RPP | - | - | -
SYSTEM A | 12 | RPPAF562 | RPP | - | - | -
SYSTEM A | 12 | RPPAF182 | RPP | - | - | -
SYSTEM A | 12 | RPPAF282 | RPP | - | - | -
SYSTEM A | 12 | RPPAF382 | RPP | - | - | -
SYSTEM A | 12 | RPPAF482 | RPP | - | - | -
SYSTEM A | 12 | RPPAF582 | RPP | - | - | -
SYSTEM A | 13 | GENAH100 | GEN | - | - | 1750kW/2187.5KVA, 480Y/277V, 3P, 4W, 0.80PF
SYSTEM A | 13 | TRNAH110 | TRN | - | - | -
SYSTEM A | 13 | ATSAH110 | ATS | TRNAH110 | - | 2500AF, 2500A, 480V, 3, , 4W, 4-POLE, 2500AT, 100%, 65kAIC, SE RATED, OPEN/DELAYED, LSIG, ERMS
SYSTEM A | 13 | MSBAH110 | MSB | - | - | 2500A, 480Y/277V, 3, , 4W, 65kAIC
SYSTEM A | 13 | TRNAH310 | TRN | - | - | 480V:208Y/120
SYSTEM A | 13 | TRNAH510 | TRN | - | - | 480V:208Y/120
SYSTEM A | 13 | TRNAH710 | TRN | - | - | 480V:208Y/120
SYSTEM A | 13 | TRNAH910 | TRN | - | - | 480V:208Y/120
SYSTEM A | 13 | ELPAH110 | ELP | TRNAH310 | - | -
SYSTEM A | 13 | ELPAH210 | ELP | TRNAH310 | TRNAH510 | -
SYSTEM A | 13 | ELPAH410 | ELP | ELPAH210 | TRNAH310, TRNAH510 | -
SYSTEM A | 13 | ELPAH510 | ELP | TRNAH510 | TRNAH710 | -
SYSTEM A | 13 | ELPAH710 | ELP | ELPAH510 | TRNAH710, TRNAH510 | -
SYSTEM A | 13 | ELPAH810 | ELP | TRNAH710 | TRNAH910 | -
SYSTEM A | 13 | ELPAH910 | ELP | TRNAH910 | - | -
SYSTEM A | 13 | EPPAH230 | EPP | ELPAH110 | ELPAH210, ELPAH410, TRNAH310 | -
SYSTEM A | 13 | EPPAH550 | EPP | ELPAH410 | ELPAH510, ELPAH210, ELPAH710, TRNAH310, TRNAH510 | -
SYSTEM A | 13 | EPPAH770 | EPP | ELPAH710 | ELPAH810, ELPAH510, TRNAH710, TRNAH910, TRNAH510 | -
SYSTEM A | 13 | TRNAH210 | TRN | EPPAH230 | ELPAH410, ELPAH110, ELPAH210, TRNAH310 | 480V:208Y/120
SYSTEM A | 13 | TRNAH440 | TRN | EPPAH550 | EPPAH230, ELPAH710, ELPAH410, ELPAH510, ELPAH210, TRNAH310, TRNAH510 | 480V:208Y/120
SYSTEM A | 13 | TRNAH670 | TRN | EPPAH770 | EPPAH550, ELPAH710, ELPAH810, ELPAH510, TRNAH710, TRNAH510 | 480V:208Y/120
SYSTEM A | 13 | TRNAH880 | TRN | EPPAH770 | ELPAH710, ELPAH810, ELPAH910, TRNAH710, TRNAH910 | 480V:208Y/120
SYSTEM A | 13 | ELPAH320 | ELP | EPPAH230 | TRNAH440, TRNAH210, EPPAH550 | -
SYSTEM A | 13 | ELPAH650 | ELP | EPPAH550 | TRNAH670, TRNAH440, EPPAH770 | -
SYSTEM A | 13 | EPPAH120 | EPP | ELPAH320 | TRNAH210, EPPAH230 | -
SYSTEM A | 13 | EPPAH320 | EPP | ELPAH320 | TRNAH210, TRNAH440, EPPAH230, EPPAH550 | -
SYSTEM A | 13 | EPPAH440 | EPP | ELPAH320 | ELPAH650, TRNAH210, TRNAH440, EPPAH230, EPPAH550 | -
SYSTEM A | 13 | EPPAH660 | EPP | ELPAH650 | TRNAH670, TRNAH880, TRNAH440, EPPAH770, EPPAH550 | -
SYSTEM A | 13 | EPPAH870 | EPP | ELPAH650 | TRNAH670, TRNAH880, EPPAH770 | -
SYSTEM A | 13 | EPPAH980 | EPP | TRNAH880 | EPPAH770, TRNAH670 | -
SYSTEM A | 13 | XPPAH120 | XPP | EPPAH120 | EPPAH320, EPPAH440 | -
SYSTEM A | 14 | GENAZ100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM A | 14 | GSBAZ110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM A | 14 | TRNAZ110 | TRN | - | - | -
SYSTEM A | 14 | GSBAC110 | GSB | GSBAD110 | - | -
SYSTEM A | 14 | GSBAD110 | GSB | - | - | -
SYSTEM A | 14 | MSBAZ110 | MSB | TRNAZ110 | - | 4000A, 480Y/277V, 3, , 4W, 100kAIC, S.E. RATED, WOODWARD PLC BREAKER TRANSFER CONTROLLER, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM A | 14 | MDPAZ110 | MDP | - | - | 600A, 480V, 3, , 3W, 65kAIC
SYSTEM A | 14 | ELPAZ110 | ELP | - | - | -
SYSTEM A | 14 | UPSAZ110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM A | 14 | UPSAZ210 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM A | 14 | TRNAZ210 | TRN | ELPAZ110 | - | 480V:208Y/120, 45KVA, NEMA 1
SYSTEM A | 14 | EPPAZ120 | EPP | TRNAZ210 | - | -
SYSTEM A | 14 | EPPAZ210 | EPP | EPPAZ120 | - | 150A, 480V, 3, , 3W, 35kAIC
SYSTEM A | 14 | UPBAZ110 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ210 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ310 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ410 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ510 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ120 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ220 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ320 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ420 | UPB | - | - | -
SYSTEM A | 14 | UPBAZ520 | UPB | - | - | -
SYSTEM A | 14 | MBCAZ110 | MBC | UPBAZ110 | UPBAZ210 | 2500AF, 2500AT, 2500A, 480V, 3, , 3W, 100kAIC, 100%
SYSTEM A | 14 | EPPAZ110 | EPP | - | - | 150A, 480V, 3, , 3W, 35kAIC
SYSTEM A | 14 | BSWAZ110 | BSW | - | - | -
SYSTEM A | 14 | BSWAZ110 | BSW | - | - | -
SYSTEM A | 14 | BSWAZ110 | BSW | - | - | -
SYSTEM A | 14 | BSWAZ210 | BSW | BSWAZ110 | BSWAZ110, BSWAZ110 | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE
SYSTEM A | 14 | BSWAZ210 | BSW | BSWAZ110 | BSWAZ110 | -
SYSTEM A | 14 | BSWAZ310 | BSW | BSWAZ210 | BSWAZ210, BSWAZ110, BSWAZ110, BSWAZ110 | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE
SYSTEM A | 14 | BSWAZ310 | BSW | BSWAZ210 | BSWAZ210, BSWAZ110 | -

## SYSTEM A
Page | Equipment | Type | Primary From | Alternate From | Properties
1 | GENAA100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
1 | GSBAA110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
1 | TRNAA110 | TRN | - | - | -
1 | GSBAB110 | GSB | - | - | -
1 | MSBAA110 | MSB | TRNAA110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
1 | MDPAA110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
1 | UPSAA110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
1 | UPSAA210 | UPS | MDPAA110 | - | 1000kVA/1000kW, 480Y/277V, 3
1 | EPPAZ110 | EPP | - | - | -
1 | EPPAZ110 | EPP | - | - | -
1 | EPPAZ110 | EPP | - | - | -
1 | TRNAA310 | TRN | - | - | 480V:208Y/120, 75KVA, NEMA 1
1 | UPBAA110 | UPB | - | - | -
1 | UPBAA210 | UPB | - | - | -
1 | UPBAA310 | UPB | - | - | -
1 | UPBAA410 | UPB | - | - | -
1 | UPBAA510 | UPB | - | - | -
1 | UPBAA120 | UPB | - | - | -
1 | UPBAA220 | UPB | - | - | -
1 | UPBAA320 | UPB | EPPAZ110 | - | -
1 | UPBAA420 | UPB | EPPAZ110 | - | -
1 | UPBAA520 | UPB | EPPAZ110 | - | -
1 | EPPAZ210 | EPP | UPBAA520 | EPPAZ110, EPPAZ110, EPPAZ110 | -
1 | EPPAZ210 | EPP | ELPAA110 | EPPAZ110, EPPAZ110, EPPAZ110 | -
1 | ELPAA110 | ELP | TRNAA310 | EPPAZ110 | -
1 | MBCAA110 | MBC | UPBAA110 | UPBAA210 | 2500AF, 2500AT
1 | TRNAA210 | TRN | EPPAA230 | ELPAA110, TRNAA310 | -
1 | EPPAA230 | EPP | ELPAA110 | TRNAA310 | -
1 | EPPAA120 | EPP | TRNAA210 | EPPAA230 | -
1 | EPPAA320 | EPP | EPPAA230 | TRNAA210 | -
1 | STSAA110 | STS | - | - | -
1 | STSAA210 | STS | - | - | -
2 | MBCAA110 | MBC | - | - | -
2 | MBCAA110 | MBC | - | - | -
2 | BSWAZ110 | BSW | MBCAA110 | - | -
2 | BSWAZ110 | BSW | MBCAA110 | - | -
2 | STSAA110 | STS | BSWAZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
2 | STSAA210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
2 | UDPAA110 | UDP | STSAA110 | - | 1600A, 480V, 3, , 3W, 65kAIC
2 | UDPAA220 | UDP | STSAA210 | - | 1600A, 480V, 3, , 3W, 65kAIC
2 | PDUAA110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
2 | PDUAA310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
2 | PDUAA520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | PDUAA720 | PDU | - | - | 500KVA, K4 RATING
2 | TRNAA410 | TRN | - | - | -
2 | RPPAA111 | RPP | - | - | -
2 | RPPAA211 | RPP | TRNAA410 | - | -
2 | RPPAA311 | RPP | TRNAA410 | - | -
2 | RPPAA411 | RPP | TRNAA410 | - | -
2 | RPPAA511 | RPP | TRNAA410 | - | -
2 | RPPAA131 | RPP | TRNAA410 | - | -
2 | RPPAA231 | RPP | TRNAA410 | - | -
2 | RPPAA331 | RPP | - | - | -
2 | RPPAA431 | RPP | - | - | -
2 | RPPAA531 | RPP | - | - | -
2 | RPPAA152 | RPP | - | - | -
2 | RPPAA252 | RPP | - | - | -
2 | RPPAA352 | RPP | - | - | -
2 | RPPAA452 | RPP | - | - | -
2 | RPPAA552 | RPP | - | - | -
2 | RPPAA172 | RPP | - | - | -
2 | RPPAA272 | RPP | - | - | -
2 | RPPAA372 | RPP | - | - | -
2 | RPPAA472 | RPP | - | - | -
2 | RPPAA572 | RPP | RPPAA472 | RPPAA372, RPPAA272, RPPAA172 | -
2 | RPPAA610 | RPP | RPPAA511 | RPPAA411, RPPAA311, RPPAA131, RPPAA211, RPPAA231, TRNAA410 | -
2 | MBCAA110 | MBC | RPPAA531 | RPPAA431, RPPAA331, RPPAA231, RPPAA152 | -
2 | UDPAA310 | UDP | MBCAA110 | RPPAA331, RPPAA431, RPPAA531, RPPAA152, RPPAA252, RPPAA352, RPPAA452, RPPAA552 | 2500A, 480V, 3, , 3W, 65kAIC
2 | BSWAZ210 | BSW | - | - | -
2 | BSWAZ310 | BSW | - | - | -
2 | BSWAZ210 | BSW | - | - | -
2 | BSWAZ310 | BSW | - | - | -
2 | ATSAA130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
2 | ATSAA230 | ATS | - | - | 800A,480V, 3, , 3-POLE
2 | ATSAA330 | ATS | BSWAZ310 | BSWAZ310 | 800A,480V, 3, , 3-POLE
2 | ATSAA430 | ATS | - | - | -
2 | PDUAA210 | PDU | ATSAA130 | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | PDUAA420 | PDU | ATSAA230 | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | PDUAA630 | PDU | ATSAA330 | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | PDUAA840 | PDU | ATSAA430 | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | RPPAA121 | RPP | RPPAA421 | RPPAA521 | -
2 | RPPAA221 | RPP | RPPAA421 | RPPAA521 | -
2 | RPPAA321 | RPP | RPPAA421 | RPPAA521 | -
2 | RPPAA421 | RPP | - | - | -
2 | RPPAA521 | RPP | RPPAA141 | - | -
2 | RPPAA141 | RPP | - | - | -
2 | RPPAA241 | RPP | - | - | -
2 | RPPAA341 | RPP | RPPAA441 | RPPAA241, RPPAA541, RPPAA141 | -
2 | RPPAA441 | RPP | RPPAA241 | RPPAA141 | -
2 | RPPAA541 | RPP | RPPAA241 | RPPAA141 | -
2 | RPPAA162 | RPP | RPPAA462 | RPPAA562 | -
2 | RPPAA262 | RPP | RPPAA462 | RPPAA562 | -
2 | RPPAA362 | RPP | RPPAA462 | RPPAA562 | -
2 | RPPAA462 | RPP | - | - | -
2 | RPPAA562 | RPP | - | - | -
2 | RPPAA182 | RPP | RPPAA382 | RPPAA482, RPPAA582 | -
2 | RPPAA282 | RPP | RPPAA382 | RPPAA482, RPPAA582 | -
2 | RPPAA382 | RPP | - | - | -
2 | RPPAA482 | RPP | - | - | -
2 | RPPAA582 | RPP | - | - | -
3 | GENAB100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
3 | GSBAB110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
3 | TRNAB110 | TRN | - | - | -
3 | GSBAA110 | GSB | - | - | -
3 | GSBAC110 | GSB | - | - | -
3 | MSBAB110 | MSB | TRNAB110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
3 | MDPAB110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
3 | UPSAB110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
3 | UPSAB210 | UPS | MDPAB110 | - | 1000kVA/1000kW, 480Y/277V, 3
3 | EPPAZ110 | EPP | - | - | -
3 | EPPAZ110 | EPP | - | - | -
3 | EPPAZ110 | EPP | - | - | -
3 | TRNAB310 | TRN | - | - | -
3 | TRNAB410 | TRN | TRNAB310 | - | 480V:480Y/277, 30KVA, NEMA 1
3 | UPBAB110 | UPB | - | - | -
3 | UPBAB210 | UPB | - | - | -
3 | UPBAB310 | UPB | - | - | -
3 | UPBAB410 | UPB | - | - | -
3 | UPBAB510 | UPB | - | - | -
3 | UPBAB120 | UPB | - | - | -
3 | UPBAB220 | UPB | - | - | -
3 | UPBAB320 | UPB | EPPAZ110 | - | -
3 | UPBAB420 | UPB | EPPAZ110 | - | -
3 | UPBAB520 | UPB | EPPAZ110 | - | -
3 | EPPAZ210 | EPP | UPBAB520 | EPPAZ110, EPPAZ110, EPPAZ110 | -
3 | EPPAZ210 | EPP | ELPAB110 | EPPAZ110, EPPAZ110, EPPAZ110 | -
3 | ELPAB110 | ELP | TRNAB310 | TRNAB410, EPPAZ110 | -
3 | EPPAB230 | EPP | ELPAB110 | TRNAB410, TRNAB310 | -
3 | MBCAB110 | MBC | UPBAB110 | UPBAB210 | 2500AF, 2500AT
3 | TRNAB210 | TRN | EPPAB230 | ELPAB110, TRNAB410, TRNAB310 | -
3 | ELPAB240 | ELP | TRNAB210 | EPPAB230, ELPAB110, TRNAB410 | -
3 | EPPAB120 | EPP | TRNAB210 | ELPAB240, EPPAB230 | -
3 | STSAB110 | STS | - | - | -
3 | STSAB210 | STS | - | - | -
4 | MBCAB110 | MBC | - | - | -
4 | MBCAB110 | MBC | - | - | -
4 | BSWAZ110 | BSW | MBCAB110 | - | -
4 | BSWAZ110 | BSW | MBCAB110 | - | -
4 | BSWAZ110 | BSW | - | - | -
4 | STSAB110 | STS | BSWAZ110 | - | 1600A, 480V, 3, 3 POLE, 65kAIC, , 3W
4 | STSAB210 | STS | - | - | 1600A, 480V, 3, 3 POLE, 65kAIC, , 3W
4 | UDPAB110 | UDP | STSAB110 | - | 1600A, 480V, 3, , 3W, 65kAIC
4 | UDPAB220 | UDP | STSAB210 | - | 1600A, 480V, 3, , 3W, 65kAIC
4 | PDUAB110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
4 | PDUAB310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
4 | PDUAB520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
4 | PDUAB720 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
4 | TRNAB550 | TRN | - | - | 415V:208Y/120, 30KVA, NEMA 1
4 | RPPAB111 | RPP | - | - | -
4 | RPPAB211 | RPP | - | - | -
4 | RPPAB311 | RPP | - | - | -
4 | RPPAB411 | RPP | - | - | -
4 | RPPAB511 | RPP | - | - | -
4 | RPPAB131 | RPP | - | - | -
4 | RPPAB231 | RPP | - | - | -
4 | RPPAB331 | RPP | - | - | -
4 | RPPAB431 | RPP | - | - | -
4 | RPPAB531 | RPP | - | - | -
4 | RPPAB152 | RPP | - | - | -
4 | RPPAB252 | RPP | TRNAB550 | - | -
4 | RPPAB352 | RPP | TRNAB550 | - | -
4 | RPPAB452 | RPP | TRNAB550 | - | -
4 | RPPAB552 | RPP | TRNAB550 | - | -
4 | RPPAB172 | RPP | TRNAB550 | - | -
4 | RPPAB272 | RPP | - | - | -
4 | RPPAB372 | RPP | - | - | -
4 | RPPAB472 | RPP | - | - | -
4 | RPPAB572 | RPP | - | - | -
4 | RPPAB650 | RPP | RPPAB552 | RPPAB452, RPPAB352, RPPAB172, RPPAB252, TRNAB550 | -
4 | MBCAB110 | MBC | RPPAB531 | RPPAB431, RPPAB331, RPPAB231, RPPAB152 | -
4 | UDPAB310 | UDP | MBCAB110 | RPPAB331, RPPAB431, RPPAB531, RPPAB152, RPPAB252, RPPAB352, RPPAB452, RPPAB552 | 2500A, 480V, 3, , 3W, 65kAIC
4 | BSWAZ210 | BSW | - | - | -
4 | BSWAZ310 | BSW | - | - | -
4 | BSWAZ210 | BSW | - | - | -
4 | BSWAZ210 | BSW | BSWAZ310 | - | -
4 | BSWAZ310 | BSW | - | - | -
4 | BSWAZ310 | BSW | - | - | -
4 | ATSAB130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
4 | ATSAB230 | ATS | - | - | 800A,480V, 3, , 3-POLE
4 | ATSAB330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
4 | ATSAB430 | ATS | - | - | 800A,480V, 3, , 3-POLE
4 | PDUAB210 | PDU | ATSAB130 | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
4 | PDUAB420 | PDU | ATSAB230 | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
4 | PDUAB630 | PDU | ATSAB330 | - | 500KVA, K4 RATING, 480V:415Y/240V
4 | PDUAB840 | PDU | ATSAB430 | - | 500KVA, K4 RATING
4 | RPPAB121 | RPP | - | - | -
4 | RPPAB221 | RPP | - | - | -
4 | RPPAB321 | RPP | - | - | -
4 | RPPAB421 | RPP | - | - | -
4 | RPPAB521 | RPP | - | - | -
4 | RPPAB141 | RPP | - | - | -
4 | RPPAB241 | RPP | - | - | -
4 | RPPAB341 | RPP | - | - | -
4 | RPPAB441 | RPP | - | - | -
4 | RPPAB541 | RPP | - | - | -
4 | RPPAB162 | RPP | - | - | -
4 | RPPAB262 | RPP | - | - | -
4 | RPPAB362 | RPP | - | - | -
4 | RPPAB462 | RPP | - | - | -
4 | RPPAB562 | RPP | - | - | -
4 | RPPAB182 | RPP | - | - | -
4 | RPPAB282 | RPP | - | - | -
4 | RPPAB382 | RPP | - | - | -
4 | RPPAB482 | RPP | - | - | -
4 | RPPAB582 | RPP | - | - | -
5 | GENAC100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
5 | GSBAC110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
5 | TRNAC110 | TRN | - | - | -
5 | GSBAB110 | GSB | - | - | -
5 | GSBAZ110 | GSB | - | - | -
5 | MSBAC110 | MSB | TRNAC110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
5 | MDPAC110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
5 | UPSAC110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
5 | UPSAC210 | UPS | MDPAC110 | - | 1000kVA/1000kW, 480Y/277V, 3
5 | EPPAZ110 | EPP | - | - | -
5 | EPPAZ110 | EPP | - | - | -
5 | EPPAZ110 | EPP | - | - | -
5 | TRNAC310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
5 | UPBAC110 | UPB | - | - | -
5 | UPBAC210 | UPB | - | - | -
5 | UPBAC310 | UPB | - | - | -
5 | UPBAC410 | UPB | - | - | -
5 | UPBAC510 | UPB | - | - | -
5 | UPBAC120 | UPB | - | - | -
5 | UPBAC220 | UPB | - | - | -
5 | UPBAC320 | UPB | EPPAZ110 | - | -
5 | UPBAC420 | UPB | EPPAZ110 | - | -
5 | UPBAC520 | UPB | EPPAZ110 | - | -
5 | EPPAZ210 | EPP | UPBAC520 | EPPAZ110, EPPAZ110, EPPAZ110 | -
5 | EPPAZ210 | EPP | EPPAZ110 | EPPAZ110, EPPAZ110 | -
5 | EPPAZ210 | EPP | ELPAC110 | EPPAZ110, EPPAZ110, EPPAZ110 | -
5 | ELPAC110 | ELP | TRNAC310 | EPPAZ110 | -
5 | MBCAC110 | MBC | UPBAC110 | UPBAC210 | 2500AF, 2500AT
5 | TRNAC210 | TRN | ELPAC110 | EPPAZ210, TRNAC310 | -
5 | ELPAC230 | ELP | TRNAC210 | ELPAC110, TRNAC310 | -
5 | EPPAC120 | EPP | TRNAC210 | ELPAC230 | -
5 | STSAC110 | STS | - | - | -
5 | STSAC210 | STS | - | - | -
6 | MBCAC110 | MBC | - | - | -
6 | MBCAC110 | MBC | - | - | -
6 | BSWAZ110 | BSW | MBCAC110 | - | -
6 | BSWAZ110 | BSW | MBCAC110 | - | -
6 | BSWAZ110 | BSW | - | - | -
6 | STSAC110 | STS | BSWAZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
6 | STSAC210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
6 | UDPAC110 | UDP | STSAC110 | - | 1600A, 480V, 3, , 3W, 65kAIC
6 | UDPAC220 | UDP | STSAC210 | - | 1600A, 480V, 3, , 3W, 65kAIC
6 | PDUAC110 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
6 | PDUAC310 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
6 | PDUAC520 | PDU | - | - | 500KVA, 480V:415Y/240V
6 | PDUAC720 | PDU | - | - | 500KVA
6 | RPPAC111 | RPP | - | - | -
6 | RPPAC211 | RPP | - | - | -
6 | RPPAC311 | RPP | - | - | -
6 | RPPAC411 | RPP | - | - | -
6 | RPPAC511 | RPP | - | - | -
6 | RPPAC131 | RPP | - | - | -
6 | RPPAC231 | RPP | - | - | -
6 | RPPAC331 | RPP | - | - | -
6 | RPPAC431 | RPP | - | - | -
6 | RPPAC531 | RPP | - | - | -
6 | RPPAC152 | RPP | - | - | -
6 | RPPAC252 | RPP | - | - | -
6 | RPPAC352 | RPP | - | - | -
6 | RPPAC452 | RPP | - | - | -
6 | RPPAC552 | RPP | - | - | -
6 | RPPAC172 | RPP | - | - | -
6 | RPPAC272 | RPP | - | - | -
6 | RPPAC372 | RPP | - | - | -
6 | RPPAC472 | RPP | - | - | -
6 | RPPAC572 | RPP | - | - | -
6 | MBCAC110 | MBC | RPPAC531 | RPPAC431, RPPAC331, RPPAC231, RPPAC152 | -
6 | UDPAC310 | UDP | MBCAC110 | RPPAC331, RPPAC431, RPPAC531, RPPAC152, RPPAC252, RPPAC352, RPPAC452, RPPAC552 | 2500A, 480V, 3, , 3W, 65kAIC
6 | BSWAZ210 | BSW | - | - | -
6 | BSWAZ310 | BSW | - | - | -
6 | BSWAZ210 | BSW | - | - | -
6 | BSWAZ210 | BSW | - | - | -
6 | BSWAZ310 | BSW | - | - | -
6 | ATSAC130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
6 | ATSAC230 | ATS | - | - | 800A,480V, 3, , 3-POLE
6 | ATSAC330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
6 | ATSAC430 | ATS | - | - | -
6 | PDUAC210 | PDU | ATSAC130 | - | 500KVA, 480V:415Y/240V
6 | PDUAC420 | PDU | ATSAC230 | - | 500KVA, 480V:415Y/240V
6 | PDUAC630 | PDU | ATSAC330 | - | 500KVA, 480V:415Y/240V
6 | PDUAC840 | PDU | ATSAC430 | - | 500KVA, 480V:415Y/240V
6 | RPPAC121 | RPP | - | - | -
6 | RPPAC221 | RPP | - | - | -
6 | RPPAC321 | RPP | - | - | -
6 | RPPAC421 | RPP | - | - | -
6 | RPPAC521 | RPP | - | - | -
6 | RPPAC141 | RPP | - | - | -
6 | RPPAC241 | RPP | - | - | -
6 | RPPAC341 | RPP | - | - | -
6 | RPPAC441 | RPP | - | - | -
6 | RPPAC541 | RPP | - | - | -
6 | RPPAC162 | RPP | - | - | -
6 | RPPAC262 | RPP | - | - | -
6 | RPPAC362 | RPP | - | - | -
6 | RPPAC462 | RPP | - | - | -
6 | RPPAC562 | RPP | - | - | -
6 | RPPAC182 | RPP | - | - | -
6 | RPPAC282 | RPP | - | - | -
6 | RPPAC382 | RPP | - | - | -
6 | RPPAC482 | RPP | - | - | -
6 | RPPAC582 | RPP | - | - | -
7 | GENAD100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
7 | GSBAD110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
7 | TRNAD110 | TRN | - | - | -
7 | GSBAZ110 | GSB | - | - | -
7 | GSBAE110 | GSB | - | - | -
7 | MSBAD110 | MSB | TRNAD110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
7 | MDPAD110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
7 | UPSAD110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
7 | UPSAD210 | UPS | MDPAD110 | - | 1000kVA/1000kW, 480Y/277V, 3
7 | EPPAZ110 | EPP | - | - | -
7 | EPPAZ110 | EPP | - | - | -
7 | EPPAZ110 | EPP | - | - | -
7 | TRNAD310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
7 | UPBAD110 | UPB | - | - | -
7 | UPBAD210 | UPB | - | - | -
7 | UPBAD310 | UPB | - | - | -
7 | UPBAD410 | UPB | - | - | -
7 | UPBAD510 | UPB | - | - | -
7 | UPBAD120 | UPB | - | - | -
7 | UPBAD220 | UPB | - | - | -
7 | UPBAD320 | UPB | EPPAZ110 | - | -
7 | UPBAD420 | UPB | EPPAZ110 | - | -
7 | UPBAD520 | UPB | EPPAZ110 | - | -
7 | EPPAZ210 | EPP | UPBAD520 | EPPAZ110, EPPAZ110, EPPAZ110 | -
7 | EPPAZ210 | EPP | EPPAZ110 | EPPAZ110, EPPAZ110 | -
7 | EPPAZ210 | EPP | ELPAD110 | EPPAZ110, EPPAZ110, EPPAZ110 | -
7 | ELPAD110 | ELP | TRNAD310 | EPPAZ110 | -
7 | MBCAD110 | MBC | UPBAD110 | UPBAD210 | 2500AF, 2500AT
7 | TRNAD210 | TRN | ELPAD110 | EPPAZ210, TRNAD310 | -
7 | ELPAD230 | ELP | TRNAD210 | ELPAD110, TRNAD310 | -
7 | EPPAD120 | EPP | TRNAD210 | ELPAD230 | -
7 | STSAD110 | STS | - | - | -
7 | STSAD210 | STS | - | - | -
8 | MBCAD110 | MBC | - | - | -
8 | MBCAD110 | MBC | - | - | -
8 | BSWAZ110 | BSW | MBCAD110 | - | -
8 | BSWAZ110 | BSW | MBCAD110 | - | -
8 | BSWAZ110 | BSW | - | - | -
8 | STSAD110 | STS | BSWAZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
8 | STSAD210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
8 | UDPAD110 | UDP | STSAD110 | - | 1600A, 480V, 3, , 3W, 65kAIC
8 | UDPAD220 | UDP | STSAD210 | - | 1600A, 480V, 3, , 3W, 65kAIC
8 | PDUAD110 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
8 | PDUAD310 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
8 | PDUAD520 | PDU | - | - | 500KVA, 480V:415Y/240V
8 | PDUAD720 | PDU | - | - | 500KVA
8 | RPPAD111 | RPP | - | - | -
8 | RPPAD211 | RPP | - | - | -
8 | RPPAD311 | RPP | - | - | -
8 | RPPAD411 | RPP | - | - | -
8 | RPPAD511 | RPP | - | - | -
8 | RPPAD131 | RPP | - | - | -
8 | RPPAD231 | RPP | - | - | -
8 | RPPAD331 | RPP | - | - | -
8 | RPPAD431 | RPP | - | - | -
8 | RPPAD531 | RPP | - | - | -
8 | RPPAD152 | RPP | - | - | -
8 | RPPAD252 | RPP | - | - | -
8 | RPPAD352 | RPP | - | - | -
8 | RPPAD452 | RPP | - | - | -
8 | RPPAD552 | RPP | - | - | -
8 | RPPAD172 | RPP | - | - | -
8 | RPPAD272 | RPP | - | - | -
8 | RPPAD372 | RPP | - | - | -
8 | RPPAD472 | RPP | - | - | -
8 | RPPAD572 | RPP | - | - | -
8 | MBCAD110 | MBC | RPPAD531 | RPPAD431, RPPAD331, RPPAD231, RPPAD152 | -
8 | UDPAD310 | UDP | MBCAD110 | RPPAD331, RPPAD431, RPPAD531, RPPAD152, RPPAD252, RPPAD352, RPPAD452, RPPAD552 | 2500A, 480V, 3, , 3W, 65kAIC
8 | BSWAZ210 | BSW | - | - | -
8 | BSWAZ310 | BSW | - | - | -
8 | BSWAZ210 | BSW | - | - | -
8 | BSWAZ210 | BSW | BSWAZ310 | - | -
8 | BSWAZ310 | BSW | - | - | -
8 | ATSAD130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
8 | ATSAD230 | ATS | - | - | 800A,480V, 3, , 3-POLE
8 | ATSAD330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
8 | ATSAD430 | ATS | - | - | -
8 | PDUAD210 | PDU | ATSAD130 | - | 500KVA, 480V:415Y/240V
8 | PDUAD420 | PDU | ATSAD230 | - | 500KVA, 480V:415Y/240V
8 | PDUAD630 | PDU | ATSAD330 | - | 500KVA, 480V:415Y/240V
8 | PDUAD840 | PDU | ATSAD430 | - | 500KVA, 480V:415Y/240V
8 | RPPAD121 | RPP | - | - | -
8 | RPPAD221 | RPP | - | - | -
8 | RPPAD321 | RPP | - | - | -
8 | RPPAD421 | RPP | - | - | -
8 | RPPAD521 | RPP | - | - | -
8 | RPPAD141 | RPP | - | - | -
8 | RPPAD241 | RPP | - | - | -
8 | RPPAD341 | RPP | - | - | -
8 | RPPAD441 | RPP | - | - | -
8 | RPPAD541 | RPP | - | - | -
8 | RPPAD162 | RPP | - | - | -
8 | RPPAD262 | RPP | - | - | -
8 | RPPAD362 | RPP | - | - | -
8 | RPPAD462 | RPP | - | - | -
8 | RPPAD562 | RPP | - | - | -
8 | RPPAD182 | RPP | - | - | -
8 | RPPAD282 | RPP | - | - | -
8 | RPPAD382 | RPP | - | - | -
8 | RPPAD482 | RPP | - | - | -
8 | RPPAD582 | RPP | - | - | -
9 | GENAE100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
9 | GSBAE110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
9 | TRNAE110 | TRN | - | - | -
9 | GSBAD110 | GSB | - | - | -
9 | GSBAF110 | GSB | - | - | -
9 | MSBAE110 | MSB | TRNAE110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
9 | MDPAE110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
9 | UPSAE110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
9 | UPSAE210 | UPS | MDPAE110 | - | 1000kVA/1000kW, 480Y/277V, 3
9 | EPPAZ110 | EPP | - | - | -
9 | EPPAZ110 | EPP | - | - | -
9 | TRNAE310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
9 | UPBAE110 | UPB | - | - | -
9 | UPBAE210 | UPB | - | - | -
9 | UPBAE310 | UPB | - | - | -
9 | UPBAE410 | UPB | - | - | -
9 | UPBAE510 | UPB | - | - | -
9 | UPBAE120 | UPB | - | - | -
9 | UPBAE220 | UPB | - | - | -
9 | UPBAE320 | UPB | EPPAZ110 | - | -
9 | UPBAE420 | UPB | EPPAZ110 | - | -
9 | UPBAE520 | UPB | EPPAZ110 | - | -
9 | EPPAZ210 | EPP | UPBAE520 | EPPAZ110, EPPAZ110 | -
9 | EPPAZ210 | EPP | ELPAE110 | EPPAZ110, EPPAZ110 | -
9 | EPPAZ210 | EPP | ELPAE110 | EPPAZ110, EPPAZ110 | -
9 | ELPAE110 | ELP | TRNAE310 | - | -
9 | MBCAE110 | MBC | UPBAE110 | UPBAE210 | 2500AF, 2500AT
9 | TRNAE210 | TRN | ELPAE110 | EPPAZ210, TRNAE310 | -
9 | ELPAE230 | ELP | TRNAE210 | ELPAE110, TRNAE310 | -
9 | EPPAE120 | EPP | TRNAE210 | ELPAE230 | -
9 | STSAE110 | STS | - | - | -
9 | STSAE210 | STS | - | - | -
10 | MBCAE110 | MBC | - | - | -
10 | MBCAE110 | MBC | - | - | -
10 | BSWAZ110 | BSW | MBCAE110 | - | -
10 | BSWAZ110 | BSW | MBCAE110 | - | -
10 | BSWAZ110 | BSW | - | - | -
10 | STSAE110 | STS | BSWAZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
10 | STSAE210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
10 | UDPAE110 | UDP | STSAE110 | - | 1600A, 480V, 3, , 3W, 65kAIC
10 | UDPAE220 | UDP | STSAE210 | - | 1600A, 480V, 3, , 3W, 65kAIC
10 | PDUAE110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
10 | PDUAE310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
10 | PDUAE520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | PDUAE720 | PDU | - | - | 500KVA, K4 RATING
10 | TRNAE450 | TRN | - | - | -
10 | RPPAE111 | RPP | - | - | -
10 | RPPAE211 | RPP | - | - | -
10 | RPPAE311 | RPP | - | - | -
10 | RPPAE411 | RPP | - | - | -
10 | RPPAE511 | RPP | - | - | -
10 | RPPAE131 | RPP | - | - | -
10 | RPPAE231 | RPP | - | - | -
10 | RPPAE331 | RPP | - | - | -
10 | RPPAE431 | RPP | - | - | -
10 | RPPAE531 | RPP | - | - | -
10 | RPPAE152 | RPP | - | - | -
10 | RPPAE252 | RPP | TRNAE450 | - | -
10 | RPPAE352 | RPP | TRNAE450 | - | -
10 | RPPAE452 | RPP | TRNAE450 | - | -
10 | RPPAE552 | RPP | TRNAE450 | - | -
10 | RPPAE172 | RPP | TRNAE450 | - | -
10 | RPPAE272 | RPP | - | - | -
10 | RPPAE372 | RPP | - | - | -
10 | RPPAE472 | RPP | - | - | -
10 | RPPAE572 | RPP | - | - | -
10 | RPPAE650 | RPP | RPPAE552 | RPPAE452, RPPAE352, RPPAE172, RPPAE252, TRNAE450 | -
10 | MBCAE110 | MBC | RPPAE531 | RPPAE431, RPPAE331, RPPAE231, RPPAE152 | -
10 | UDPAE310 | UDP | MBCAE110 | RPPAE331, RPPAE431, RPPAE531, RPPAE152, RPPAE252, RPPAE352, RPPAE452, RPPAE552 | 2500A, 480V, 3, , 3W, 65kAIC
10 | RPPAE760 | RPP | RPPAE650 | - | -
10 | BSWAZ210 | BSW | - | - | -
10 | BSWAZ310 | BSW | - | - | -
10 | BSWAZ210 | BSW | - | - | -
10 | BSWAZ210 | BSW | BSWAZ310 | - | -
10 | BSWAZ310 | BSW | - | - | -
10 | ATSAE130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
10 | ATSAE230 | ATS | - | - | 800A,480V, 3, , 3-POLE
10 | ATSAE330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
10 | ATSAE430 | ATS | - | - | -
10 | PDUAE210 | PDU | ATSAE130 | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | PDUAE420 | PDU | ATSAE230 | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | PDUAE630 | PDU | ATSAE330 | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | PDUAE840 | PDU | ATSAE430 | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | RPPAE121 | RPP | - | - | -
10 | RPPAE221 | RPP | - | - | -
10 | RPPAE321 | RPP | - | - | -
10 | RPPAE421 | RPP | - | - | -
10 | RPPAE521 | RPP | - | - | -
10 | RPPAE141 | RPP | - | - | -
10 | RPPAE241 | RPP | - | - | -
10 | RPPAE341 | RPP | - | - | -
10 | RPPAE441 | RPP | - | - | -
10 | RPPAE541 | RPP | - | - | -
10 | RPPAE162 | RPP | - | - | -
10 | RPPAE262 | RPP | - | - | -
10 | RPPAE362 | RPP | - | - | -
10 | RPPAE462 | RPP | - | - | -
10 | RPPAE562 | RPP | - | - | -
10 | RPPAE182 | RPP | - | - | -
10 | RPPAE282 | RPP | - | - | -
10 | RPPAE382 | RPP | - | - | -
10 | RPPAE482 | RPP | - | - | -
10 | RPPAE582 | RPP | - | - | -
11 | GENAF100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
11 | GSBAF110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
11 | TRNAF110 | TRN | - | - | -
11 | GSBAE110 | GSB | - | - | -
11 | MSBAF110 | MSB | TRNAF110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
11 | MDPAF110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
11 | UPSAF110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
11 | UPSAF210 | UPS | MDPAF110 | - | 1000kVA/1000kW, 480Y/277V, 3
11 | EPPAZ110 | EPP | - | - | -
11 | EPPAZ110 | EPP | - | - | -
11 | TRNAF310 | TRN | - | - | 480V:208Y/120, 75KVA, NEMA 1
11 | UPBAF110 | UPB | - | - | -
11 | UPBAF210 | UPB | - | - | -
11 | UPBAF310 | UPB | - | - | -
11 | UPBAF410 | UPB | - | - | -
11 | UPBAF510 | UPB | - | - | -
11 | UPBAF120 | UPB | - | - | -
11 | UPBAF220 | UPB | - | - | -
11 | UPBAF320 | UPB | EPPAZ110 | - | -
11 | UPBAF420 | UPB | EPPAZ110 | - | -
11 | UPBAF520 | UPB | EPPAZ110 | - | -
11 | EPPAZ210 | EPP | UPBAF520 | EPPAZ110, EPPAZ110 | -
11 | EPPAZ210 | EPP | ELPAF110 | EPPAZ110, EPPAZ110 | -
11 | EPPAZ210 | EPP | ELPAF110 | EPPAZ110, EPPAZ110 | -
11 | ELPAF110 | ELP | TRNAF310 | - | -
11 | MBCAF110 | MBC | UPBAF110 | UPBAF210 | 2500AF, 2500AT
11 | TRNAF210 | TRN | EPPAF230 | EPPAZ210, ELPAF110, TRNAF310 | -
11 | EPPAF230 | EPP | ELPAF110 | TRNAF310 | -
11 | EPPAF120 | EPP | TRNAF210 | EPPAF230 | -
11 | EPPAF320 | EPP | EPPAF230 | TRNAF210 | -
11 | STSAF110 | STS | - | - | -
11 | STSAF210 | STS | - | - | -
12 | MBCAF110 | MBC | - | - | -
12 | MBCAF110 | MBC | - | - | -
12 | BSWAZ110 | BSW | MBCAF110 | - | -
12 | BSWAZ110 | BSW | - | - | -
12 | STSAF110 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
12 | STSAF210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
12 | UDPAF110 | UDP | STSAF110 | - | 1600A, 480V, 3, , 3W, 65kAIC
12 | UDPAF220 | UDP | STSAF210 | - | 1600A, 480V, 3, , 3W, 65kAIC
12 | PDUAF110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
12 | PDUAF310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
12 | PDUAF520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | PDUAF720 | PDU | - | - | 500KVA, K4 RATING
12 | TRNAF410 | TRN | - | - | -
12 | RPPAF111 | RPP | - | - | -
12 | RPPAF211 | RPP | TRNAF410 | - | -
12 | RPPAF311 | RPP | TRNAF410 | - | -
12 | RPPAF411 | RPP | TRNAF410 | - | -
12 | RPPAF511 | RPP | TRNAF410 | - | -
12 | RPPAF131 | RPP | TRNAF410 | - | -
12 | RPPAF231 | RPP | TRNAF410 | - | -
12 | RPPAF331 | RPP | - | - | -
12 | RPPAF431 | RPP | - | - | -
12 | RPPAF531 | RPP | - | - | -
12 | RPPAF152 | RPP | - | - | -
12 | RPPAF252 | RPP | - | - | -
12 | RPPAF352 | RPP | - | - | -
12 | RPPAF452 | RPP | - | - | -
12 | RPPAF552 | RPP | - | - | -
12 | RPPAF172 | RPP | - | - | -
12 | RPPAF272 | RPP | - | - | -
12 | RPPAF372 | RPP | - | - | -
12 | RPPAF472 | RPP | - | - | -
12 | RPPAF572 | RPP | - | - | -
12 | RPPAF610 | RPP | RPPAF511 | RPPAF411, RPPAF311, RPPAF131, RPPAF211, RPPAF231, TRNAF410 | -
12 | MBCAF110 | MBC | RPPAF531 | RPPAF431, RPPAF331, RPPAF231, RPPAF152 | -
12 | UDPAF310 | UDP | MBCAF110 | RPPAF331, RPPAF431, RPPAF531, RPPAF152, RPPAF252, RPPAF352, RPPAF452, RPPAF552 | 2500A, 480V, 3, , 3W, 65kAIC
12 | RPPAF760 | RPP | RPPAF610 | - | -
12 | BSWAZ210 | BSW | - | - | -
12 | BSWAZ310 | BSW | - | - | -
12 | BSWAZ210 | BSW | - | - | -
12 | BSWAZ210 | BSW | - | - | -
12 | BSWAZ310 | BSW | - | - | -
12 | ATSAF130 | ATS | BSWAZ210 | BSWAZ210 | 800A,480V, 3, , 3-POLE
12 | ATSAF230 | ATS | - | - | 800A,480V, 3, , 3-POLE
12 | ATSAF330 | ATS | BSWAZ310 | BSWAZ210, BSWAZ310 | 800A,480V, 3, , 3-POLE
12 | ATSAF430 | ATS | - | - | -
12 | PDUAF210 | PDU | ATSAF130 | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | PDUAF420 | PDU | ATSAF230 | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | PDUAF630 | PDU | ATSAF330 | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | PDUAF840 | PDU | ATSAF430 | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | RPPAF121 | RPP | - | - | -
12 | RPPAF221 | RPP | - | - | -
12 | RPPAF321 | RPP | - | - | -
12 | RPPAF421 | RPP | - | - | -
12 | RPPAF521 | RPP | - | - | -
12 | RPPAF141 | RPP | - | - | -
12 | RPPAF241 | RPP | - | - | -
12 | RPPAF341 | RPP | - | - | -
12 | RPPAF441 | RPP | - | - | -
12 | RPPAF541 | RPP | - | - | -
12 | RPPAF162 | RPP | - | - | -
12 | RPPAF262 | RPP | - | - | -
12 | RPPAF362 | RPP | - | - | -
12 | RPPAF462 | RPP | - | - | -
12 | RPPAF562 | RPP | - | - | -
12 | RPPAF182 | RPP | - | - | -
12 | RPPAF282 | RPP | - | - | -
12 | RPPAF382 | RPP | - | - | -
12 | RPPAF482 | RPP | - | - | -
12 | RPPAF582 | RPP | - | - | -
13 | GENAH100 | GEN | - | - | 1750kW/2187.5KVA, 480Y/277V, 3P, 4W, 0.80PF
13 | TRNAH110 | TRN | - | - | -
13 | ATSAH110 | ATS | TRNAH110 | - | 2500AF, 2500A, 480V, 3, , 4W, 4-POLE, 2500AT, 100%, 65kAIC, SE RATED, OPEN/DELAYED, LSIG, ERMS
13 | MSBAH110 | MSB | - | - | 2500A, 480Y/277V, 3, , 4W, 65kAIC
13 | TRNAH310 | TRN | - | - | 480V:208Y/120
13 | TRNAH510 | TRN | - | - | 480V:208Y/120
13 | TRNAH710 | TRN | - | - | 480V:208Y/120
13 | TRNAH910 | TRN | - | - | 480V:208Y/120
13 | ELPAH110 | ELP | TRNAH310 | - | -
13 | ELPAH210 | ELP | TRNAH310 | TRNAH510 | -
13 | ELPAH410 | ELP | ELPAH210 | TRNAH310, TRNAH510 | -
13 | ELPAH510 | ELP | TRNAH510 | TRNAH710 | -
13 | ELPAH710 | ELP | ELPAH510 | TRNAH710, TRNAH510 | -
13 | ELPAH810 | ELP | TRNAH710 | TRNAH910 | -
13 | ELPAH910 | ELP | TRNAH910 | - | -
13 | EPPAH230 | EPP | ELPAH110 | ELPAH210, ELPAH410, TRNAH310 | -
13 | EPPAH550 | EPP | ELPAH410 | ELPAH510, ELPAH210, ELPAH710, TRNAH310, TRNAH510 | -
13 | EPPAH770 | EPP | ELPAH710 | ELPAH810, ELPAH510, TRNAH710, TRNAH910, TRNAH510 | -
13 | TRNAH210 | TRN | EPPAH230 | ELPAH410, ELPAH110, ELPAH210, TRNAH310 | 480V:208Y/120
13 | TRNAH440 | TRN | EPPAH550 | EPPAH230, ELPAH710, ELPAH410, ELPAH510, ELPAH210, TRNAH310, TRNAH510 | 480V:208Y/120
13 | TRNAH670 | TRN | EPPAH770 | EPPAH550, ELPAH710, ELPAH810, ELPAH510, TRNAH710, TRNAH510 | 480V:208Y/120
13 | TRNAH880 | TRN | EPPAH770 | ELPAH710, ELPAH810, ELPAH910, TRNAH710, TRNAH910 | 480V:208Y/120
13 | ELPAH320 | ELP | EPPAH230 | TRNAH440, TRNAH210, EPPAH550 | -
13 | ELPAH650 | ELP | EPPAH550 | TRNAH670, TRNAH440, EPPAH770 | -
13 | EPPAH120 | EPP | ELPAH320 | TRNAH210, EPPAH230 | -
13 | EPPAH320 | EPP | ELPAH320 | TRNAH210, TRNAH440, EPPAH230, EPPAH550 | -
13 | EPPAH440 | EPP | ELPAH320 | ELPAH650, TRNAH210, TRNAH440, EPPAH230, EPPAH550 | -
13 | EPPAH660 | EPP | ELPAH650 | TRNAH670, TRNAH880, TRNAH440, EPPAH770, EPPAH550 | -
13 | EPPAH870 | EPP | ELPAH650 | TRNAH670, TRNAH880, EPPAH770 | -
13 | EPPAH980 | EPP | TRNAH880 | EPPAH770, TRNAH670 | -
13 | XPPAH120 | XPP | EPPAH120 | EPPAH320, EPPAH440 | -
14 | GENAZ100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
14 | GSBAZ110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
14 | TRNAZ110 | TRN | - | - | -
14 | GSBAC110 | GSB | GSBAD110 | - | -
14 | GSBAD110 | GSB | - | - | -
14 | MSBAZ110 | MSB | TRNAZ110 | - | 4000A, 480Y/277V, 3, , 4W, 100kAIC, S.E. RATED, WOODWARD PLC BREAKER TRANSFER CONTROLLER, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
14 | MDPAZ110 | MDP | - | - | 600A, 480V, 3, , 3W, 65kAIC
14 | ELPAZ110 | ELP | - | - | -
14 | UPSAZ110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
14 | UPSAZ210 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3
14 | TRNAZ210 | TRN | ELPAZ110 | - | 480V:208Y/120, 45KVA, NEMA 1
14 | EPPAZ120 | EPP | TRNAZ210 | - | -
14 | EPPAZ210 | EPP | EPPAZ120 | - | 150A, 480V, 3, , 3W, 35kAIC
14 | UPBAZ110 | UPB | - | - | -
14 | UPBAZ210 | UPB | - | - | -
14 | UPBAZ310 | UPB | - | - | -
14 | UPBAZ410 | UPB | - | - | -
14 | UPBAZ510 | UPB | - | - | -
14 | UPBAZ120 | UPB | - | - | -
14 | UPBAZ220 | UPB | - | - | -
14 | UPBAZ320 | UPB | - | - | -
14 | UPBAZ420 | UPB | - | - | -
14 | UPBAZ520 | UPB | - | - | -
14 | MBCAZ110 | MBC | UPBAZ110 | UPBAZ210 | 2500AF, 2500AT, 2500A, 480V, 3, , 3W, 100kAIC, 100%
14 | EPPAZ110 | EPP | - | - | 150A, 480V, 3, , 3W, 35kAIC
14 | BSWAZ110 | BSW | - | - | -
14 | BSWAZ110 | BSW | - | - | -
14 | BSWAZ110 | BSW | - | - | -
14 | BSWAZ210 | BSW | BSWAZ110 | BSWAZ110, BSWAZ110 | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE
14 | BSWAZ210 | BSW | BSWAZ110 | BSWAZ110 | -
14 | BSWAZ310 | BSW | BSWAZ210 | BSWAZ210, BSWAZ110, BSWAZ110, BSWAZ110 | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE
14 | BSWAZ310 | BSW | BSWAZ210 | BSWAZ210, BSWAZ110 | -