## All Systems
System | Page | Equipment | Type | Primary From | Alternate From | Properties
SYSTEM B | 1 | GENBA100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM B | 1 | GSBBA110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM B | 1 | TRNBA110 | TRN | - | - | -
SYSTEM B | 1 | GSBBB110 | GSB | - | - | -
SYSTEM B | 1 | MSBBA110 | MSB | TRNBA110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM B | 1 | MDPBA110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM B | 1 | UPSBA110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM B | 1 | UPSBA210 | UPS | MDPBA110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM B | 1 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 1 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 1 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 1 | TRNBA310 | TRN | - | - | 480V:208Y/120, 75KVA, NEMA 1
SYSTEM B | 1 | UPBBA110 | UPB | - | - | -
SYSTEM B | 1 | UPBBA210 | UPB | - | - | -
SYSTEM B | 1 | UPBBA310 | UPB | - | - | -
SYSTEM B | 1 | UPBBA410 | UPB | - | - | -
SYSTEM B | 1 | UPBBA510 | UPB | - | - | -
SYSTEM B | 1 | UPBBA120 | UPB | - | - | -
SYSTEM B | 1 | UPBBA220 | UPB | - | - | -
SYSTEM B | 1 | UPBBA320 | UPB | EPPBZ110 | - | -
SYSTEM B | 1 | UPBBA420 | UPB | EPPBZ110 | - | -
SYSTEM B | 1 | UPBBA520 | UPB | EPPBZ110 | - | -
SYSTEM B | 1 | EPPBZ210 | EPP | UPBBA520 | EPPBZ110, EPPBZ110, EPPBZ110 | -
SYSTEM B | 1 | EPPBZ210 | EPP | ELPBA110 | EPPBZ110, EPPBZ110, EPPBZ110 | -
SYSTEM B | 1 | ELPBA110 | ELP | TRNBA310 | EPPBZ110 | -
SYSTEM B | 1 | MBCBA110 | MBC | UPBBA110 | UPBBA210 | 2500AF, 2500AT
SYSTEM B | 1 | TRNBA210 | TRN | EPPBA230 | ELPBA110, TRNBA310 | -
SYSTEM B | 1 | EPPBA230 | EPP | ELPBA110 | TRNBA310 | -
SYSTEM B | 1 | EPPBA120 | EPP | TRNBA210 | EPPBA230 | -
SYSTEM B | 1 | EPPBA320 | EPP | EPPBA230 | TRNBA210 | -
SYSTEM B | 1 | STSBA110 | STS | - | - | -
SYSTEM B | 1 | STSBA210 | STS | - | - | -
SYSTEM B | 2 | MBCBA110 | MBC | - | - | -
SYSTEM B | 2 | MBCBA110 | MBC | - | - | -
SYSTEM B | 2 | BSWBZ110 | BSW | MBCBA110 | - | -
SYSTEM B | 2 | BSWBZ110 | BSW | MBCBA110 | - | -
SYSTEM B | 2 | STSBA110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 2 | STSBA210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 2 | UDPBA110 | UDP | STSBA110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 2 | UDPBA220 | UDP | STSBA210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 2 | PDUBA110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM B | 2 | PDUBA310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM B | 2 | PDUBA520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 2 | PDUBA720 | PDU | - | - | 500KVA, K4 RATING
SYSTEM B | 2 | TRNBA410 | TRN | - | - | -
SYSTEM B | 2 | RPPBA113 | RPP | - | - | -
SYSTEM B | 2 | RPPBA213 | RPP | TRNBA410 | - | -
SYSTEM B | 2 | RPPBA313 | RPP | TRNBA410 | - | -
SYSTEM B | 2 | RPPBA413 | RPP | TRNBA410 | - | -
SYSTEM B | 2 | RPPBA513 | RPP | TRNBA410 | - | -
SYSTEM B | 2 | RPPBA133 | RPP | TRNBA410 | - | -
SYSTEM B | 2 | RPPBA233 | RPP | TRNBA410 | - | -
SYSTEM B | 2 | RPPBA333 | RPP | - | - | -
SYSTEM B | 2 | RPPBA433 | RPP | - | - | -
SYSTEM B | 2 | RPPBA533 | RPP | - | - | -
SYSTEM B | 2 | RPPBA154 | RPP | - | - | -
SYSTEM B | 2 | RPPBA254 | RPP | - | - | -
SYSTEM B | 2 | RPPBA354 | RPP | - | - | -
SYSTEM B | 2 | RPPBA454 | RPP | - | - | -
SYSTEM B | 2 | RPPBA554 | RPP | - | - | -
SYSTEM B | 2 | RPPBA174 | RPP | - | - | -
SYSTEM B | 2 | RPPBA274 | RPP | - | - | -
SYSTEM B | 2 | RPPBA374 | RPP | - | - | -
SYSTEM B | 2 | RPPBA474 | RPP | - | - | -
SYSTEM B | 2 | RPPBA574 | RPP | - | - | -
SYSTEM B | 2 | RPPBA610 | RPP | RPPBA513 | RPPBA413, RPPBA313, RPPBA133, RPPBA213, RPPBA233, TRNBA410 | -
SYSTEM B | 2 | MBCBA110 | MBC | RPPBA533 | RPPBA433, RPPBA333, RPPBA233, RPPBA154 | -
SYSTEM B | 2 | UDPBA310 | UDP | MBCBA110 | RPPBA333, RPPBA433, RPPBA533, RPPBA154, RPPBA254, RPPBA354, RPPBA454, RPPBA554 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 2 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 2 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 2 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 2 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 2 | ATSBA130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
SYSTEM B | 2 | ATSBA230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM B | 2 | ATSBA330 | ATS | BSWBZ310 | BSWBZ310 | 800A,480V, 3, , 3-POLE
SYSTEM B | 2 | ATSBA430 | ATS | - | - | -
SYSTEM B | 2 | PDUBA210 | PDU | ATSBA130 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 2 | PDUBA420 | PDU | ATSBA230 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 2 | PDUBA630 | PDU | ATSBA330 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 2 | PDUBA840 | PDU | ATSBA430 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 2 | RPPBA123 | RPP | - | - | -
SYSTEM B | 2 | RPPBA223 | RPP | - | - | -
SYSTEM B | 2 | RPPBA323 | RPP | - | - | -
SYSTEM B | 2 | RPPBA423 | RPP | - | - | -
SYSTEM B | 2 | RPPBA523 | RPP | - | - | -
SYSTEM B | 2 | RPPBA143 | RPP | - | - | -
SYSTEM B | 2 | RPPBA243 | RPP | - | - | -
SYSTEM B | 2 | RPPBA343 | RPP | - | - | -
SYSTEM B | 2 | RPPBA443 | RPP | - | - | -
SYSTEM B | 2 | RPPBA543 | RPP | - | - | -
SYSTEM B | 2 | RPPBA164 | RPP | - | - | -
SYSTEM B | 2 | RPPBA264 | RPP | - | - | -
SYSTEM B | 2 | RPPBA364 | RPP | - | - | -
SYSTEM B | 2 | RPPBA464 | RPP | - | - | -
SYSTEM B | 2 | RPPBA564 | RPP | - | - | -
SYSTEM B | 2 | RPPBA184 | RPP | - | - | -
SYSTEM B | 2 | RPPBA284 | RPP | - | - | -
SYSTEM B | 2 | RPPBA384 | RPP | - | - | -
SYSTEM B | 2 | RPPBA484 | RPP | - | - | -
SYSTEM B | 2 | RPPBA584 | RPP | - | - | -
SYSTEM B | 3 | GENBB100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM B | 3 | GSBBB110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM B | 3 | TRNBB110 | TRN | - | - | -
SYSTEM B | 3 | GSBBA110 | GSB | - | - | -
SYSTEM B | 3 | GSBBC110 | GSB | - | - | -
SYSTEM B | 3 | MSBBB110 | MSB | TRNBB110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM B | 3 | MDPBB110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM B | 3 | UPSBB110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM B | 3 | UPSBB210 | UPS | MDPBB110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM B | 3 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 3 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 3 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 3 | TRNBB310 | TRN | - | - | -
SYSTEM B | 3 | TRNBB410 | TRN | TRNBB310 | - | 480V:480Y/277, 30KVA, NEMA 1
SYSTEM B | 3 | UPBBB110 | UPB | - | - | -
SYSTEM B | 3 | UPBBB210 | UPB | - | - | -
SYSTEM B | 3 | UPBBB310 | UPB | - | - | -
SYSTEM B | 3 | UPBBB410 | UPB | - | - | -
SYSTEM B | 3 | UPBBB510 | UPB | - | - | -
SYSTEM B | 3 | UPBBB120 | UPB | - | - | -
SYSTEM B | 3 | UPBBB220 | UPB | - | - | -
SYSTEM B | 3 | UPBBB320 | UPB | EPPBZ110 | - | -
SYSTEM B | 3 | UPBBB420 | UPB | EPPBZ110 | - | -
SYSTEM B | 3 | UPBBB520 | UPB | EPPBZ110 | - | -
SYSTEM B | 3 | EPPBZ210 | EPP | UPBBB520 | EPPBZ110, EPPBZ110, EPPBZ110 | -
SYSTEM B | 3 | EPPBZ210 | EPP | ELPBB110 | EPPBZ110, EPPBZ110, EPPBZ110 | -
SYSTEM B | 3 | ELPBB110 | ELP | TRNBB310 | TRNBB410, EPPBZ110 | -
SYSTEM B | 3 | EPPBB230 | EPP | ELPBB110 | TRNBB410, TRNBB310 | -
SYSTEM B | 3 | MBCBB110 | MBC | UPBBB110 | UPBBB210 | 2500AF, 2500AT
SYSTEM B | 3 | TRNBB210 | TRN | EPPBB230 | ELPBB110, TRNBB410, TRNBB310 | -
SYSTEM B | 3 | ELPBB240 | ELP | TRNBB210 | EPPBB230, ELPBB110, TRNBB410 | -
SYSTEM B | 3 | EPPBB120 | EPP | TRNBB210 | ELPBB240, EPPBB230 | -
SYSTEM B | 3 | STSBB110 | STS | - | - | -
SYSTEM B | 3 | STSBB210 | STS | - | - | -
SYSTEM B | 4 | MBCBB110 | MBC | - | - | -
SYSTEM B | 4 | MBCBB110 | MBC | - | - | -
SYSTEM B | 4 | BSWBZ110 | BSW | MBCBB110 | - | -
SYSTEM B | 4 | BSWBZ110 | BSW | MBCBB110 | - | -
SYSTEM B | 4 | BSWBZ110 | BSW | - | - | -
SYSTEM B | 4 | STSBB110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 4 | STSBB210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 4 | UDPBB110 | UDP | STSBB110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 4 | UDPBB220 | UDP | STSBB210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 4 | PDUBB110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM B | 4 | PDUBB310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM B | 4 | PDUBB520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 4 | PDUBB720 | PDU | - | - | 500KVA, K4 RATING
SYSTEM B | 4 | TRNBB550 | TRN | - | - | -
SYSTEM B | 4 | RPPBB113 | RPP | - | - | -
SYSTEM B | 4 | RPPBB213 | RPP | - | - | -
SYSTEM B | 4 | RPPBB313 | RPP | - | - | -
SYSTEM B | 4 | RPPBB413 | RPP | - | - | -
SYSTEM B | 4 | RPPBB513 | RPP | - | - | -
SYSTEM B | 4 | RPPBB133 | RPP | - | - | -
SYSTEM B | 4 | RPPBB233 | RPP | - | - | -
SYSTEM B | 4 | RPPBB333 | RPP | - | - | -
SYSTEM B | 4 | RPPBB433 | RPP | - | - | -
SYSTEM B | 4 | RPPBB533 | RPP | - | - | -
SYSTEM B | 4 | RPPBB154 | RPP | - | - | -
SYSTEM B | 4 | RPPBB254 | RPP | TRNBB550 | - | -
SYSTEM B | 4 | RPPBB354 | RPP | TRNBB550 | - | -
SYSTEM B | 4 | RPPBB454 | RPP | TRNBB550 | - | -
SYSTEM B | 4 | RPPBB554 | RPP | TRNBB550 | - | -
SYSTEM B | 4 | RPPBB174 | RPP | TRNBB550 | - | -
SYSTEM B | 4 | RPPBB274 | RPP | - | - | -
SYSTEM B | 4 | RPPBB374 | RPP | - | - | -
SYSTEM B | 4 | RPPBB474 | RPP | - | - | -
SYSTEM B | 4 | RPPBB574 | RPP | - | - | -
SYSTEM B | 4 | RPPBB650 | RPP | RPPBB554 | RPPBB454, RPPBB354, RPPBB174, RPPBB254, TRNBB550 | -
SYSTEM B | 4 | MBCBB110 | MBC | RPPBB533 | RPPBB433, RPPBB333, RPPBB233, RPPBB154 | -
SYSTEM B | 4 | UDPBB310 | UDP | MBCBB110 | RPPBB333, RPPBB433, RPPBB533, RPPBB154, RPPBB254, RPPBB354, RPPBB454, RPPBB554 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 4 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 4 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 4 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 4 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 4 | BSWBZ310 | BSW | BSWBZ210 | - | -
SYSTEM B | 4 | ATSBB130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
SYSTEM B | 4 | ATSBB230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM B | 4 | ATSBB330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
SYSTEM B | 4 | ATSBB430 | ATS | - | - | -
SYSTEM B | 4 | PDUBB210 | PDU | ATSBB130 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 4 | PDUBB420 | PDU | ATSBB230 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 4 | PDUBB630 | PDU | ATSBB330 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 4 | PDUBB840 | PDU | ATSBB430 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 4 | RPPBB123 | RPP | - | - | -
SYSTEM B | 4 | RPPBB223 | RPP | - | - | -
SYSTEM B | 4 | RPPBB323 | RPP | - | - | -
SYSTEM B | 4 | RPPBB423 | RPP | - | - | -
SYSTEM B | 4 | RPPBB523 | RPP | - | - | -
SYSTEM B | 4 | RPPBB143 | RPP | - | - | -
SYSTEM B | 4 | RPPBB243 | RPP | - | - | -
SYSTEM B | 4 | RPPBB343 | RPP | - | - | -
SYSTEM B | 4 | RPPBB443 | RPP | - | - | -
SYSTEM B | 4 | RPPBB543 | RPP | - | - | -
SYSTEM B | 4 | RPPBB164 | RPP | - | - | -
SYSTEM B | 4 | RPPBB264 | RPP | - | - | -
SYSTEM B | 4 | RPPBB364 | RPP | - | - | -
SYSTEM B | 4 | RPPBB464 | RPP | - | - | -
SYSTEM B | 4 | RPPBB564 | RPP | - | - | -
SYSTEM B | 4 | RPPBB184 | RPP | - | - | -
SYSTEM B | 4 | RPPBB284 | RPP | - | - | -
SYSTEM B | 4 | RPPBB384 | RPP | - | - | -
SYSTEM B | 4 | RPPBB484 | RPP | - | - | -
SYSTEM B | 4 | RPPBB584 | RPP | - | - | -
SYSTEM B | 5 | GENBC100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM B | 5 | GSBBC110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM B | 5 | TRNBC110 | TRN | - | - | -
SYSTEM B | 5 | GSBBB110 | GSB | - | - | -
SYSTEM B | 5 | GSBBZ110 | GSB | - | - | -
SYSTEM B | 5 | MSBBC110 | MSB | TRNBC110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM B | 5 | MDPBC110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM B | 5 | UPSBC110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM B | 5 | UPSBC210 | UPS | MDPBC110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM B | 5 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 5 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 5 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 5 | TRNBC310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
SYSTEM B | 5 | UPBBC110 | UPB | - | - | -
SYSTEM B | 5 | UPBBC210 | UPB | - | - | -
SYSTEM B | 5 | UPBBC310 | UPB | - | - | -
SYSTEM B | 5 | UPBBC410 | UPB | - | - | -
SYSTEM B | 5 | UPBBC510 | UPB | - | - | -
SYSTEM B | 5 | UPBBC120 | UPB | - | - | -
SYSTEM B | 5 | UPBBC220 | UPB | - | - | -
SYSTEM B | 5 | UPBBC320 | UPB | EPPBZ110 | - | -
SYSTEM B | 5 | UPBBC420 | UPB | EPPBZ110 | - | -
SYSTEM B | 5 | UPBBC520 | UPB | EPPBZ110 | - | -
SYSTEM B | 5 | EPPBZ210 | EPP | UPBBC520 | EPPBZ110, EPPBZ110, EPPBZ110 | -
SYSTEM B | 5 | EPPBZ210 | EPP | EPPBZ110 | EPPBZ110, EPPBZ110 | -
SYSTEM B | 5 | EPPBZ210 | EPP | ELPBC110 | EPPBZ110, EPPBZ110, EPPBZ110 | -
SYSTEM B | 5 | ELPBC110 | ELP | TRNBC310 | EPPBZ110 | -
SYSTEM B | 5 | MBCBC110 | MBC | UPBBC110 | UPBBC210 | 2500AF, 2500AT
SYSTEM B | 5 | TRNBC210 | TRN | ELPBC110 | EPPBZ210, TRNBC310 | -
SYSTEM B | 5 | ELPBC230 | ELP | TRNBC210 | ELPBC110, TRNBC310 | -
SYSTEM B | 5 | EPPBC120 | EPP | TRNBC210 | ELPBC230 | -
SYSTEM B | 5 | STSBC110 | STS | - | - | -
SYSTEM B | 5 | STSBC210 | STS | - | - | -
SYSTEM B | 6 | MBCBC110 | MBC | - | - | -
SYSTEM B | 6 | MBCBC110 | MBC | - | - | -
SYSTEM B | 6 | BSWBZ110 | BSW | MBCBC110 | - | -
SYSTEM B | 6 | BSWBZ110 | BSW | MBCBC110 | - | -
SYSTEM B | 6 | BSWBZ110 | BSW | - | - | -
SYSTEM B | 6 | STSBC110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 6 | STSBC210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 6 | UDPBC110 | UDP | STSBC110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 6 | UDPBC220 | UDP | STSBC210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 6 | PDUBC110 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
SYSTEM B | 6 | PDUBC310 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
SYSTEM B | 6 | PDUBC520 | PDU | - | - | 500KVA, 480V:415Y/240V
SYSTEM B | 6 | PDUBC720 | PDU | - | - | 500KVA
SYSTEM B | 6 | RPPBC113 | RPP | - | - | -
SYSTEM B | 6 | RPPBC213 | RPP | - | - | -
SYSTEM B | 6 | RPPBC313 | RPP | - | - | -
SYSTEM B | 6 | RPPBC413 | RPP | - | - | -
SYSTEM B | 6 | RPPBC513 | RPP | - | - | -
SYSTEM B | 6 | RPPBC133 | RPP | - | - | -
SYSTEM B | 6 | RPPBC233 | RPP | - | - | -
SYSTEM B | 6 | RPPBC333 | RPP | - | - | -
SYSTEM B | 6 | RPPBC433 | RPP | - | - | -
SYSTEM B | 6 | RPPBC533 | RPP | - | - | -
SYSTEM B | 6 | RPPBC154 | RPP | - | - | -
SYSTEM B | 6 | RPPBC254 | RPP | - | - | -
SYSTEM B | 6 | RPPBC354 | RPP | - | - | -
SYSTEM B | 6 | RPPBC454 | RPP | - | - | -
SYSTEM B | 6 | RPPBC554 | RPP | - | - | -
SYSTEM B | 6 | RPPBC174 | RPP | - | - | -
SYSTEM B | 6 | RPPBC274 | RPP | - | - | -
SYSTEM B | 6 | RPPBC374 | RPP | - | - | -
SYSTEM B | 6 | RPPBC474 | RPP | - | - | -
SYSTEM B | 6 | RPPBC574 | RPP | - | - | -
SYSTEM B | 6 | MBCBC110 | MBC | RPPBC533 | RPPBC433, RPPBC333, RPPBC233, RPPBC154 | -
SYSTEM B | 6 | UDPBC310 | UDP | MBCBC110 | RPPBC333, RPPBC433, RPPBC533, RPPBC154, RPPBC254, RPPBC354, RPPBC454, RPPBC554 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 6 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 6 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 6 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 6 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 6 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 6 | ATSBC130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
SYSTEM B | 6 | ATSBC230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM B | 6 | ATSBC330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
SYSTEM B | 6 | ATSBC430 | ATS | - | - | -
SYSTEM B | 6 | PDUBC210 | PDU | ATSBC130 | - | 500KVA, 480V:415Y/240V
SYSTEM B | 6 | PDUBC420 | PDU | ATSBC230 | - | 500KVA, 480V:415Y/240V
SYSTEM B | 6 | PDUBC630 | PDU | ATSBC330 | - | 500KVA, 480V:415Y/240V
SYSTEM B | 6 | PDUBC840 | PDU | ATSBC430 | - | 500KVA, 480V:415Y/240V
SYSTEM B | 6 | RPPBC123 | RPP | - | - | -
SYSTEM B | 6 | RPPBC223 | RPP | - | - | -
SYSTEM B | 6 | RPPBC323 | RPP | - | - | -
SYSTEM B | 6 | RPPBC423 | RPP | - | - | -
SYSTEM B | 6 | RPPBC523 | RPP | - | - | -
SYSTEM B | 6 | RPPBC143 | RPP | - | - | -
SYSTEM B | 6 | RPPBC243 | RPP | - | - | -
SYSTEM B | 6 | RPPBC343 | RPP | - | - | -
SYSTEM B | 6 | RPPBC443 | RPP | - | - | -
SYSTEM B | 6 | RPPBC543 | RPP | - | - | -
SYSTEM B | 6 | RPPBC164 | RPP | - | - | -
SYSTEM B | 6 | RPPBC264 | RPP | - | - | -
SYSTEM B | 6 | RPPBC364 | RPP | - | - | -
SYSTEM B | 6 | RPPBC464 | RPP | - | - | -
SYSTEM B | 6 | RPPBC564 | RPP | - | - | -
SYSTEM B | 6 | RPPBC184 | RPP | - | - | -
SYSTEM B | 6 | RPPBC284 | RPP | - | - | -
SYSTEM B | 6 | RPPBC384 | RPP | - | - | -
SYSTEM B | 6 | RPPBC484 | RPP | - | - | -
SYSTEM B | 6 | RPPBC584 | RPP | - | - | -
SYSTEM B | 7 | GENBD100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM B | 7 | GSBBD110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM B | 7 | TRNBD110 | TRN | - | - | -
SYSTEM B | 7 | GSBBZ110 | GSB | - | - | -
SYSTEM B | 7 | GSBBE110 | GSB | - | - | -
SYSTEM B | 7 | MSBBD110 | MSB | TRNBD110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM B | 7 | MDPBD110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM B | 7 | UPSBD110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM B | 7 | UPSBD210 | UPS | MDPBD110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM B | 7 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 7 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 7 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 7 | TRNBD310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
SYSTEM B | 7 | UPBBD110 | UPB | - | - | -
SYSTEM B | 7 | UPBBD210 | UPB | - | - | -
SYSTEM B | 7 | UPBBD310 | UPB | - | - | -
SYSTEM B | 7 | UPBBD410 | UPB | - | - | -
SYSTEM B | 7 | UPBBD510 | UPB | - | - | -
SYSTEM B | 7 | UPBBD120 | UPB | - | - | -
SYSTEM B | 7 | UPBBD220 | UPB | - | - | -
SYSTEM B | 7 | UPBBD320 | UPB | EPPBZ110 | - | -
SYSTEM B | 7 | UPBBD420 | UPB | EPPBZ110 | - | -
SYSTEM B | 7 | UPBBD520 | UPB | EPPBZ110 | - | -
SYSTEM B | 7 | EPPBZ210 | EPP | UPBBD520 | EPPBZ110, EPPBZ110, EPPBZ110 | -
SYSTEM B | 7 | EPPBZ210 | EPP | EPPBZ110 | EPPBZ110, EPPBZ110 | -
SYSTEM B | 7 | EPPBZ210 | EPP | ELPBD110 | EPPBZ110, EPPBZ110, EPPBZ110 | -
SYSTEM B | 7 | ELPBD110 | ELP | TRNBD310 | EPPBZ110 | -
SYSTEM B | 7 | MBCBD110 | MBC | UPBBD110 | UPBBD210 | 2500AF, 2500AT
SYSTEM B | 7 | TRNBD210 | TRN | ELPBD110 | EPPBZ210, TRNBD310 | -
SYSTEM B | 7 | ELPBD230 | ELP | TRNBD210 | ELPBD110, TRNBD310 | -
SYSTEM B | 7 | EPPBD120 | EPP | TRNBD210 | ELPBD230 | -
SYSTEM B | 7 | STSBD110 | STS | - | - | -
SYSTEM B | 7 | STSBD210 | STS | - | - | -
SYSTEM B | 8 | MBCBD110 | MBC | - | - | -
SYSTEM B | 8 | MBCBD110 | MBC | - | - | -
SYSTEM B | 8 | BSWBZ110 | BSW | MBCBD110 | - | -
SYSTEM B | 8 | BSWBZ110 | BSW | MBCBD110 | - | -
SYSTEM B | 8 | BSWBZ110 | BSW | - | - | -
SYSTEM B | 8 | STSBD110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 8 | STSBD210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 8 | UDPBD110 | UDP | STSBD110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 8 | UDPBD220 | UDP | STSBD210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 8 | PDUBD110 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
SYSTEM B | 8 | PDUBD310 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
SYSTEM B | 8 | PDUBD520 | PDU | - | - | 500KVA, 480V:415Y/240V
SYSTEM B | 8 | PDUBD720 | PDU | - | - | 500KVA
SYSTEM B | 8 | RPPBD113 | RPP | - | - | -
SYSTEM B | 8 | RPPBD213 | RPP | - | - | -
SYSTEM B | 8 | RPPBD313 | RPP | - | - | -
SYSTEM B | 8 | RPPBD413 | RPP | - | - | -
SYSTEM B | 8 | RPPBD513 | RPP | - | - | -
SYSTEM B | 8 | RPPBD133 | RPP | - | - | -
SYSTEM B | 8 | RPPBD233 | RPP | - | - | -
SYSTEM B | 8 | RPPBD333 | RPP | - | - | -
SYSTEM B | 8 | RPPBD433 | RPP | - | - | -
SYSTEM B | 8 | RPPBD533 | RPP | - | - | -
SYSTEM B | 8 | RPPBD154 | RPP | - | - | -
SYSTEM B | 8 | RPPBD254 | RPP | - | - | -
SYSTEM B | 8 | RPPBD354 | RPP | - | - | -
SYSTEM B | 8 | RPPBD454 | RPP | - | - | -
SYSTEM B | 8 | RPPBD554 | RPP | - | - | -
SYSTEM B | 8 | RPPBD174 | RPP | - | - | -
SYSTEM B | 8 | RPPBD274 | RPP | - | - | -
SYSTEM B | 8 | RPPBD374 | RPP | - | - | -
SYSTEM B | 8 | RPPBD474 | RPP | - | - | -
SYSTEM B | 8 | RPPBD574 | RPP | - | - | -
SYSTEM B | 8 | MBCBD110 | MBC | RPPBD533 | RPPBD433, RPPBD333, RPPBD233, RPPBD154 | -
SYSTEM B | 8 | UDPBD310 | UDP | MBCBD110 | RPPBD333, RPPBD433, RPPBD533, RPPBD154, RPPBD254, RPPBD354, RPPBD454, RPPBD554 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 8 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 8 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 8 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 8 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 8 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 8 | ATSBD130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
SYSTEM B | 8 | ATSBD230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM B | 8 | ATSBD330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
SYSTEM B | 8 | ATSBD430 | ATS | - | - | -
SYSTEM B | 8 | PDUBD210 | PDU | ATSBD130 | - | 500KVA, 480V:415Y/240V
SYSTEM B | 8 | PDUBD420 | PDU | ATSBD230 | - | 500KVA, 480V:415Y/240V
SYSTEM B | 8 | PDUBD630 | PDU | ATSBD330 | - | 500KVA, 480V:415Y/240V
SYSTEM B | 8 | PDUBD840 | PDU | ATSBD430 | - | 500KVA, 480V:415Y/240V
SYSTEM B | 8 | RPPBD123 | RPP | - | - | -
SYSTEM B | 8 | RPPBD223 | RPP | - | - | -
SYSTEM B | 8 | RPPBD323 | RPP | - | - | -
SYSTEM B | 8 | RPPBD423 | RPP | - | - | -
SYSTEM B | 8 | RPPBD523 | RPP | - | - | -
SYSTEM B | 8 | RPPBD143 | RPP | - | - | -
SYSTEM B | 8 | RPPBD243 | RPP | - | - | -
SYSTEM B | 8 | RPPBD343 | RPP | - | - | -
SYSTEM B | 8 | RPPBD443 | RPP | - | - | -
SYSTEM B | 8 | RPPBD543 | RPP | - | - | -
SYSTEM B | 8 | RPPBD164 | RPP | - | - | -
SYSTEM B | 8 | RPPBD264 | RPP | - | - | -
SYSTEM B | 8 | RPPBD364 | RPP | - | - | -
SYSTEM B | 8 | RPPBD464 | RPP | - | - | -
SYSTEM B | 8 | RPPBD564 | RPP | - | - | -
SYSTEM B | 8 | RPPBD184 | RPP | - | - | -
SYSTEM B | 8 | RPPBD284 | RPP | - | - | -
SYSTEM B | 8 | RPPBD384 | RPP | - | - | -
SYSTEM B | 8 | RPPBD484 | RPP | - | - | -
SYSTEM B | 8 | RPPBD584 | RPP | - | - | -
SYSTEM B | 9 | GENBE100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM B | 9 | GSBBE110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM B | 9 | TRNBE110 | TRN | - | - | -
SYSTEM B | 9 | GSBBD110 | GSB | - | - | -
SYSTEM B | 9 | GSBBF110 | GSB | - | - | -
SYSTEM B | 9 | MSBBE110 | MSB | TRNBE110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM B | 9 | MDPBE110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM B | 9 | UPSBE110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM B | 9 | UPSBE210 | UPS | MDPBE110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM B | 9 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 9 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 9 | TRNBE310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
SYSTEM B | 9 | UPBBE110 | UPB | - | - | -
SYSTEM B | 9 | UPBBE210 | UPB | - | - | -
SYSTEM B | 9 | UPBBE310 | UPB | - | - | -
SYSTEM B | 9 | UPBBE410 | UPB | - | - | -
SYSTEM B | 9 | UPBBE510 | UPB | - | - | -
SYSTEM B | 9 | UPBBE120 | UPB | - | - | -
SYSTEM B | 9 | UPBBE220 | UPB | - | - | -
SYSTEM B | 9 | UPBBE320 | UPB | EPPBZ110 | - | -
SYSTEM B | 9 | UPBBE420 | UPB | EPPBZ110 | - | -
SYSTEM B | 9 | UPBBE520 | UPB | EPPBZ110 | - | -
SYSTEM B | 9 | EPPBZ210 | EPP | UPBBE520 | EPPBZ110, EPPBZ110 | -
SYSTEM B | 9 | EPPBZ210 | EPP | ELPBE110 | EPPBZ110, EPPBZ110 | -
SYSTEM B | 9 | EPPBZ210 | EPP | ELPBE110 | EPPBZ110, EPPBZ110 | -
SYSTEM B | 9 | ELPBE110 | ELP | TRNBE310 | - | -
SYSTEM B | 9 | MBCBE110 | MBC | UPBBE110 | UPBBE210 | 2500AF, 2500AT
SYSTEM B | 9 | TRNBE210 | TRN | ELPBE110 | EPPBZ210, TRNBE310 | -
SYSTEM B | 9 | ELPBE230 | ELP | TRNBE210 | ELPBE110, TRNBE310 | -
SYSTEM B | 9 | EPPBE120 | EPP | TRNBE210 | ELPBE230 | -
SYSTEM B | 9 | STSBE110 | STS | - | - | -
SYSTEM B | 9 | STSBE210 | STS | - | - | -
SYSTEM B | 10 | MBCBE110 | MBC | - | - | -
SYSTEM B | 10 | MBCBE110 | MBC | - | - | -
SYSTEM B | 10 | BSWBZ110 | BSW | MBCBE110 | - | -
SYSTEM B | 10 | BSWBZ110 | BSW | MBCBE110 | - | -
SYSTEM B | 10 | BSWBZ110 | BSW | - | - | -
SYSTEM B | 10 | STSBE110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 10 | STSBE210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 10 | UDPBE110 | UDP | STSBE110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 10 | UDPBE220 | UDP | STSBE210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 10 | PDUBE110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM B | 10 | PDUBE310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM B | 10 | PDUBE520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 10 | PDUBE720 | PDU | - | - | 500KVA, K4 RATING
SYSTEM B | 10 | TRNBE450 | TRN | - | - | -
SYSTEM B | 10 | RPPBE113 | RPP | - | - | -
SYSTEM B | 10 | RPPBE213 | RPP | - | - | -
SYSTEM B | 10 | RPPBE313 | RPP | - | - | -
SYSTEM B | 10 | RPPBE413 | RPP | - | - | -
SYSTEM B | 10 | RPPBE513 | RPP | - | - | -
SYSTEM B | 10 | RPPBE133 | RPP | - | - | -
SYSTEM B | 10 | RPPBE233 | RPP | - | - | -
SYSTEM B | 10 | RPPBE333 | RPP | - | - | -
SYSTEM B | 10 | RPPBE433 | RPP | - | - | -
SYSTEM B | 10 | RPPBE533 | RPP | - | - | -
SYSTEM B | 10 | RPPBE154 | RPP | - | - | -
SYSTEM B | 10 | RPPBE254 | RPP | TRNBE450 | - | -
SYSTEM B | 10 | RPPBE354 | RPP | TRNBE450 | - | -
SYSTEM B | 10 | RPPBE454 | RPP | TRNBE450 | - | -
SYSTEM B | 10 | RPPBE554 | RPP | TRNBE450 | - | -
SYSTEM B | 10 | RPPBE174 | RPP | TRNBE450 | - | -
SYSTEM B | 10 | RPPBE274 | RPP | - | - | -
SYSTEM B | 10 | RPPBE374 | RPP | - | - | -
SYSTEM B | 10 | RPPBE474 | RPP | - | - | -
SYSTEM B | 10 | RPPBE574 | RPP | - | - | -
SYSTEM B | 10 | RPPBE650 | RPP | RPPBE554 | RPPBE454, RPPBE354, RPPBE174, RPPBE254, TRNBE450 | -
SYSTEM B | 10 | MBCBE110 | MBC | RPPBE533 | RPPBE433, RPPBE333, RPPBE233, RPPBE154 | -
SYSTEM B | 10 | UDPBE310 | UDP | MBCBE110 | RPPBE333, RPPBE433, RPPBE533, RPPBE154, RPPBE254, RPPBE354, RPPBE454, RPPBE554 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 10 | RPPBE760 | RPP | RPPBE650 | - | -
SYSTEM B | 10 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 10 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 10 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 10 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 10 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 10 | ATSBE130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
SYSTEM B | 10 | ATSBE230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM B | 10 | ATSBE330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
SYSTEM B | 10 | ATSBE430 | ATS | - | - | -
SYSTEM B | 10 | PDUBE210 | PDU | ATSBE130 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 10 | PDUBE420 | PDU | ATSBE230 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 10 | PDUBE630 | PDU | ATSBE330 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 10 | PDUBE840 | PDU | ATSBE430 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 10 | RPPBE123 | RPP | - | - | -
SYSTEM B | 10 | RPPBE223 | RPP | - | - | -
SYSTEM B | 10 | RPPBE323 | RPP | - | - | -
SYSTEM B | 10 | RPPBE423 | RPP | - | - | -
SYSTEM B | 10 | RPPBE523 | RPP | - | - | -
SYSTEM B | 10 | RPPBE143 | RPP | - | - | -
SYSTEM B | 10 | RPPBE243 | RPP | - | - | -
SYSTEM B | 10 | RPPBE343 | RPP | - | - | -
SYSTEM B | 10 | RPPBE443 | RPP | - | - | -
SYSTEM B | 10 | RPPBE543 | RPP | - | - | -
SYSTEM B | 10 | RPPBE164 | RPP | - | - | -
SYSTEM B | 10 | RPPBE264 | RPP | - | - | -
SYSTEM B | 10 | RPPBE364 | RPP | - | - | -
SYSTEM B | 10 | RPPBE464 | RPP | - | - | -
SYSTEM B | 10 | RPPBE564 | RPP | - | - | -
SYSTEM B | 10 | RPPBE184 | RPP | - | - | -
SYSTEM B | 10 | RPPBE284 | RPP | - | - | -
SYSTEM B | 10 | RPPBE384 | RPP | - | - | -
SYSTEM B | 10 | RPPBE484 | RPP | - | - | -
SYSTEM B | 10 | RPPBE584 | RPP | - | - | -
SYSTEM B | 11 | GENBF100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM B | 11 | GSBBF110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM B | 11 | TRNBF110 | TRN | - | - | -
SYSTEM B | 11 | GSBBE110 | GSB | - | - | -
SYSTEM B | 11 | MSBBF110 | MSB | TRNBF110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM B | 11 | MDPBF110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
SYSTEM B | 11 | UPSBF110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM B | 11 | UPSBF210 | UPS | MDPBF110 | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM B | 11 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 11 | EPPBZ110 | EPP | - | - | -
SYSTEM B | 11 | TRNBF310 | TRN | - | - | -
SYSTEM B | 11 | UPBBF110 | UPB | - | - | -
SYSTEM B | 11 | UPBBF210 | UPB | - | - | -
SYSTEM B | 11 | UPBBF310 | UPB | - | - | -
SYSTEM B | 11 | UPBBF410 | UPB | - | - | -
SYSTEM B | 11 | UPBBF510 | UPB | - | - | -
SYSTEM B | 11 | UPBBF120 | UPB | - | - | -
SYSTEM B | 11 | UPBBF220 | UPB | - | - | -
SYSTEM B | 11 | UPBBF320 | UPB | EPPBZ110 | - | -
SYSTEM B | 11 | UPBBF420 | UPB | EPPBZ110 | - | -
SYSTEM B | 11 | UPBBF520 | UPB | EPPBZ110 | - | -
SYSTEM B | 11 | EPPBZ210 | EPP | UPBBF520 | EPPBZ110, EPPBZ110 | -
SYSTEM B | 11 | EPPBZ210 | EPP | ELPBF110 | EPPBZ110, EPPBZ110 | -
SYSTEM B | 11 | EPPBZ210 | EPP | ELPBF110 | EPPBZ110, EPPBZ110 | -
SYSTEM B | 11 | ELPBF110 | ELP | TRNBF310 | - | -
SYSTEM B | 11 | MBCBF110 | MBC | UPBBF110 | UPBBF210 | 2500AF, 2500AT
SYSTEM B | 11 | TRNBF210 | TRN | EPPBF230 | EPPBZ210, ELPBF110, TRNBF310 | -
SYSTEM B | 11 | EPPBF230 | EPP | ELPBF110 | TRNBF310 | -
SYSTEM B | 11 | EPPBF120 | EPP | TRNBF210 | EPPBF230 | -
SYSTEM B | 11 | EPPBF320 | EPP | EPPBF230 | TRNBF210 | -
SYSTEM B | 11 | STSBF110 | STS | - | - | -
SYSTEM B | 11 | STSBF210 | STS | - | - | -
SYSTEM B | 12 | MBCBF110 | MBC | - | - | -
SYSTEM B | 12 | MBCBF110 | MBC | - | - | -
SYSTEM B | 12 | BSWBZ110 | BSW | MBCBF110 | - | -
SYSTEM B | 12 | BSWBZ110 | BSW | - | - | -
SYSTEM B | 12 | STSBF110 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 12 | STSBF210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
SYSTEM B | 12 | UDPBF110 | UDP | STSBF110 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 12 | UDPBF220 | UDP | STSBF210 | - | 1600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 12 | PDUBF110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM B | 12 | PDUBF310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
SYSTEM B | 12 | PDUBF520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 12 | PDUBF720 | PDU | - | - | 500KVA, K4 RATING
SYSTEM B | 12 | TRNBF410 | TRN | - | - | -
SYSTEM B | 12 | RPPBF113 | RPP | - | - | -
SYSTEM B | 12 | RPPBF213 | RPP | TRNBF410 | - | -
SYSTEM B | 12 | RPPBF313 | RPP | TRNBF410 | - | -
SYSTEM B | 12 | RPPBF413 | RPP | TRNBF410 | - | -
SYSTEM B | 12 | RPPBF513 | RPP | TRNBF410 | - | -
SYSTEM B | 12 | RPPBF133 | RPP | TRNBF410 | - | -
SYSTEM B | 12 | RPPBF233 | RPP | TRNBF410 | - | -
SYSTEM B | 12 | RPPBF333 | RPP | - | - | -
SYSTEM B | 12 | RPPBF433 | RPP | - | - | -
SYSTEM B | 12 | RPPBF533 | RPP | - | - | -
SYSTEM B | 12 | RPPBF154 | RPP | - | - | -
SYSTEM B | 12 | RPPBF254 | RPP | - | - | -
SYSTEM B | 12 | RPPBF354 | RPP | - | - | -
SYSTEM B | 12 | RPPBF454 | RPP | - | - | -
SYSTEM B | 12 | RPPBF554 | RPP | - | - | -
SYSTEM B | 12 | RPPBF174 | RPP | - | - | -
SYSTEM B | 12 | RPPBF274 | RPP | - | - | -
SYSTEM B | 12 | RPPBF374 | RPP | - | - | -
SYSTEM B | 12 | RPPBF474 | RPP | - | - | -
SYSTEM B | 12 | RPPBF574 | RPP | - | - | -
SYSTEM B | 12 | RPPBF610 | RPP | RPPBF513 | RPPBF413, RPPBF313, RPPBF133, RPPBF213, RPPBF233, TRNBF410 | -
SYSTEM B | 12 | MBCBF110 | MBC | RPPBF533 | RPPBF433, RPPBF333, RPPBF233, RPPBF154 | -
SYSTEM B | 12 | UDPBF310 | UDP | MBCBF110 | RPPBF333, RPPBF433, RPPBF533, RPPBF154, RPPBF254, RPPBF354, RPPBF454, RPPBF554 | 2500A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 12 | RPPBF760 | RPP | RPPBF610 | - | -
SYSTEM B | 12 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 12 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 12 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 12 | BSWBZ210 | BSW | - | - | -
SYSTEM B | 12 | BSWBZ310 | BSW | - | - | -
SYSTEM B | 12 | ATSBF130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
SYSTEM B | 12 | ATSBF230 | ATS | - | - | 800A,480V, 3, , 3-POLE
SYSTEM B | 12 | ATSBF330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
SYSTEM B | 12 | ATSBF430 | ATS | - | - | -
SYSTEM B | 12 | PDUBF210 | PDU | ATSBF130 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 12 | PDUBF420 | PDU | ATSBF230 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 12 | PDUBF630 | PDU | ATSBF330 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 12 | PDUBF840 | PDU | ATSBF430 | - | 500KVA, K4 RATING, 480V:415Y/240V
SYSTEM B | 12 | RPPBF123 | RPP | - | - | -
SYSTEM B | 12 | RPPBF223 | RPP | - | - | -
SYSTEM B | 12 | RPPBF323 | RPP | - | - | -
SYSTEM B | 12 | RPPBF423 | RPP | - | - | -
SYSTEM B | 12 | RPPBF523 | RPP | - | - | -
SYSTEM B | 12 | RPPBF143 | RPP | - | - | -
SYSTEM B | 12 | RPPBF243 | RPP | - | - | -
SYSTEM B | 12 | RPPBF343 | RPP | - | - | -
SYSTEM B | 12 | RPPBF443 | RPP | - | - | -
SYSTEM B | 12 | RPPBF543 | RPP | - | - | -
SYSTEM B | 12 | RPPBF164 | RPP | - | - | -
SYSTEM B | 12 | RPPBF264 | RPP | - | - | -
SYSTEM B | 12 | RPPBF364 | RPP | - | - | -
SYSTEM B | 12 | RPPBF464 | RPP | - | - | -
SYSTEM B | 12 | RPPBF564 | RPP | - | - | -
SYSTEM B | 12 | RPPBF184 | RPP | - | - | -
SYSTEM B | 12 | RPPBF284 | RPP | - | - | -
SYSTEM B | 12 | RPPBF384 | RPP | - | - | -
SYSTEM B | 12 | RPPBF484 | RPP | - | - | -
SYSTEM B | 12 | RPPBF584 | RPP | - | - | -
SYSTEM B | 13 | GENBH100 | GEN | - | - | 1750kW/2187.5KVA, 480Y/277V, 3P, 4W, 0.80PF
SYSTEM B | 13 | TRNBH110 | TRN | - | - | -
SYSTEM B | 13 | ATSBH110 | ATS | TRNBH110 | - | 2500AF, 2500A, 480V, 3, , 4W, 4-POLE, 2500AT, 65kAIC, SE RATED, OPEN/DELAYED, 100%, LSIG, ERMS
SYSTEM B | 13 | MSBBH110 | MSB | - | - | 2500A, 480Y/277V, 3, , 4W, 65kAIC
SYSTEM B | 13 | TRNBH310 | TRN | - | - | 480V:208Y/120, PANEL, 75KVA, NEMA 1
SYSTEM B | 13 | TRNBH510 | TRN | - | - | 480V:208Y/120, PANEL, 75KVA, NEMA 1
SYSTEM B | 13 | TRNBH710 | TRN | - | - | 480V:208Y/120, PANEL
SYSTEM B | 13 | TRNBH910 | TRN | - | - | 480V:208Y/120
SYSTEM B | 13 | ELPBH110 | ELP | TRNBH310 | - | -
SYSTEM B | 13 | ELPBH210 | ELP | TRNBH310 | TRNBH510 | -
SYSTEM B | 13 | ELPBH410 | ELP | TRNBH310 | TRNBH510 | -
SYSTEM B | 13 | ELPBH510 | ELP | TRNBH510 | TRNBH710 | -
SYSTEM B | 13 | ELPBH710 | ELP | TRNBH510 | TRNBH710 | -
SYSTEM B | 13 | ELPBH810 | ELP | TRNBH710 | TRNBH910 | -
SYSTEM B | 13 | EPPBH230 | EPP | ELPBH110 | ELPBH210, ELPBH410, TRNBH310 | -
SYSTEM B | 13 | EPPBH550 | EPP | ELPBH410 | ELPBH510, ELPBH210, ELPBH710, TRNBH310, TRNBH510 | -
SYSTEM B | 13 | EPPBH770 | EPP | ELPBH710 | ELPBH810, ELPBH510, TRNBH510, TRNBH710 | -
SYSTEM B | 13 | TRNBH210 | TRN | EPPBH230 | ELPBH110, ELPBH210, ELPBH410, TRNBH310 | 480V:208Y/120, 75KVA, NEMA 1
SYSTEM B | 13 | TRNBH440 | TRN | EPPBH550 | EPPBH230, ELPBH210, ELPBH410, ELPBH510, ELPBH710, TRNBH310, TRNBH510 | 480V:208Y/120, 75KVA, NEMA 1
SYSTEM B | 13 | TRNBH670 | TRN | EPPBH770 | EPPBH550, ELPBH510, ELPBH710, ELPBH810, TRNBH510, TRNBH710 | 480V:208Y/120, 75KVA, NEMA 1
SYSTEM B | 13 | ELPBH320 | ELP | EPPBH230 | TRNBH440, TRNBH210, EPPBH550 | -
SYSTEM B | 13 | ELPBH650 | ELP | EPPBH550 | TRNBH670, TRNBH440, EPPBH770 | -
SYSTEM B | 13 | ELPBH980 | ELP | EPPBH770 | TRNBH670 | -
SYSTEM B | 13 | EPPBH120 | EPP | ELPBH320 | TRNBH210, EPPBH230 | -
SYSTEM B | 13 | EPPBH320 | EPP | ELPBH320 | TRNBH210, TRNBH440, EPPBH230, EPPBH550 | -
SYSTEM B | 13 | EPPBH440 | EPP | ELPBH320 | ELPBH650, TRNBH210, TRNBH440, EPPBH230, EPPBH550 | -
SYSTEM B | 13 | EPPBH660 | EPP | ELPBH650 | ELPBH980, TRNBH440, TRNBH670, EPPBH550, EPPBH770 | -
SYSTEM B | 13 | EPPBH870 | EPP | ELPBH980 | ELPBH650, TRNBH670, EPPBH770 | -
SYSTEM B | 13 | EPPBH980 | EPP | ELPBH980 | TRNBH670, EPPBH770 | -
SYSTEM B | 13 | MSBBH110 | MSB | EPPBH660 | EPPBH870, EPPBH980, ELPBH650, ELPBH980 | -
SYSTEM B | 13 | MSBAH110 | MSB | - | - | (ROOF)
SYSTEM B | 13 | UPSBH110 | UPS | - | - | BIB 150A LSI, 80kVA/80kW, N.C. (2) AUX, RECTIFIER, 480V, 3, 208Y/120V, 3, , 3W, INPUT
SYSTEM B | 13 | UPPBH110 | UPP | - | - | -
SYSTEM B | 14 | GENBZ100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
SYSTEM B | 14 | GSBBZ110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
SYSTEM B | 14 | TRNBZ110 | TRN | - | - | -
SYSTEM B | 14 | GSBBC110 | GSB | GSBBD110 | - | -
SYSTEM B | 14 | GSBBD110 | GSB | - | - | -
SYSTEM B | 14 | MSBBZ110 | MSB | TRNBZ110 | - | 4000A, 480Y/277V, 3, , 4W, 100kAIC, S.E. RATED, WOODWARD PLC BREAKER TRANSFER CONTROLLER, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
SYSTEM B | 14 | MDPBZ110 | MDP | - | - | 600A, 480V, 3, , 3W, 65kAIC
SYSTEM B | 14 | ELPBZ110 | ELP | - | - | -
SYSTEM B | 14 | UPSBZ110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
SYSTEM B | 14 | UPSBZ210 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3
SYSTEM B | 14 | TRNBZ210 | TRN | ELPBZ110 | - | 480V:208Y/120, 45KVA, NEMA 1
SYSTEM B | 14 | EPPBZ120 | EPP | TRNBZ210 | - | -
SYSTEM B | 14 | EPPBZ210 | EPP | EPPBZ120 | - | 150A, 480V, 3, , 3W, 35kAIC
SYSTEM B | 14 | UPBBZ110 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ210 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ310 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ410 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ510 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ120 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ220 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ320 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ420 | UPB | - | - | -
SYSTEM B | 14 | UPBBZ520 | UPB | - | - | -
SYSTEM B | 14 | MBCBZ110 | MBC | UPBBZ110 | UPBBZ210 | 2500AF, 2500AT, 2500A, 480V, 3, , 3W, 100kAIC, 100%
SYSTEM B | 14 | EPPBZ110 | EPP | - | - | 150A, 480V, 3, , 3W, 35kAIC
SYSTEM B | 14 | BSWBZ110 | BSW | - | - | -
SYSTEM B | 14 | BSWBZ110 | BSW | - | - | -
SYSTEM B | 14 | BSWBZ110 | BSW | - | - | -
SYSTEM B | 14 | BSWBZ210 | BSW | BSWBZ110 | BSWBZ110, BSWBZ110 | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE
SYSTEM B | 14 | BSWBZ210 | BSW | BSWBZ110 | BSWBZ110 | -
SYSTEM B | 14 | BSWBZ310 | BSW | BSWBZ210 | BSWBZ210, BSWBZ110, BSWBZ110, BSWBZ110 | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE
SYSTEM B | 14 | BSWBZ310 | BSW | BSWBZ210 | BSWBZ210, BSWBZ110 | -

## SYSTEM B
Page | Equipment | Type | Primary From | Alternate From | Properties
1 | GENBA100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
1 | GSBBA110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
1 | TRNBA110 | TRN | - | - | -
1 | GSBBB110 | GSB | - | - | -
1 | MSBBA110 | MSB | TRNBA110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
1 | MDPBA110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
1 | UPSBA110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
1 | UPSBA210 | UPS | MDPBA110 | - | 1000kVA/1000kW, 480Y/277V, 3
1 | EPPBZ110 | EPP | - | - | -
1 | EPPBZ110 | EPP | - | - | -
1 | EPPBZ110 | EPP | - | - | -
1 | TRNBA310 | TRN | - | - | 480V:208Y/120, 75KVA, NEMA 1
1 | UPBBA110 | UPB | - | - | -
1 | UPBBA210 | UPB | - | - | -
1 | UPBBA310 | UPB | - | - | -
1 | UPBBA410 | UPB | - | - | -
1 | UPBBA510 | UPB | - | - | -
1 | UPBBA120 | UPB | - | - | -
1 | UPBBA220 | UPB | - | - | -
1 | UPBBA320 | UPB | EPPBZ110 | - | -
1 | UPBBA420 | UPB | EPPBZ110 | - | -
1 | UPBBA520 | UPB | EPPBZ110 | - | -
1 | EPPBZ210 | EPP | UPBBA520 | EPPBZ110, EPPBZ110, EPPBZ110 | -
1 | EPPBZ210 | EPP | ELPBA110 | EPPBZ110, EPPBZ110, EPPBZ110 | -
1 | ELPBA110 | ELP | TRNBA310 | EPPBZ110 | -
1 | MBCBA110 | MBC | UPBBA110 | UPBBA210 | 2500AF, 2500AT
1 | TRNBA210 | TRN | EPPBA230 | ELPBA110, TRNBA310 | -
1 | EPPBA230 | EPP | ELPBA110 | TRNBA310 | -
1 | EPPBA120 | EPP | TRNBA210 | EPPBA230 | -
1 | EPPBA320 | EPP | EPPBA230 | TRNBA210 | -
1 | STSBA110 | STS | - | - | -
1 | STSBA210 | STS | - | - | -
2 | MBCBA110 | MBC | - | - | -
2 | MBCBA110 | MBC | - | - | -
2 | BSWBZ110 | BSW | MBCBA110 | - | -
2 | BSWBZ110 | BSW | MBCBA110 | - | -
2 | STSBA110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
2 | STSBA210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
2 | UDPBA110 | UDP | STSBA110 | - | 1600A, 480V, 3, , 3W, 65kAIC
2 | UDPBA220 | UDP | STSBA210 | - | 1600A, 480V, 3, , 3W, 65kAIC
2 | PDUBA110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
2 | PDUBA310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
2 | PDUBA520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | PDUBA720 | PDU | - | - | 500KVA, K4 RATING
2 | TRNBA410 | TRN | - | - | -
2 | RPPBA113 | RPP | - | - | -
2 | RPPBA213 | RPP | TRNBA410 | - | -
2 | RPPBA313 | RPP | TRNBA410 | - | -
2 | RPPBA413 | RPP | TRNBA410 | - | -
2 | RPPBA513 | RPP | TRNBA410 | - | -
2 | RPPBA133 | RPP | TRNBA410 | - | -
2 | RPPBA233 | RPP | TRNBA410 | - | -
2 | RPPBA333 | RPP | - | - | -
2 | RPPBA433 | RPP | - | - | -
2 | RPPBA533 | RPP | - | - | -
2 | RPPBA154 | RPP | - | - | -
2 | RPPBA254 | RPP | - | - | -
2 | RPPBA354 | RPP | - | - | -
2 | RPPBA454 | RPP | - | - | -
2 | RPPBA554 | RPP | - | - | -
2 | RPPBA174 | RPP | - | - | -
2 | RPPBA274 | RPP | - | - | -
2 | RPPBA374 | RPP | - | - | -
2 | RPPBA474 | RPP | - | - | -
2 | RPPBA574 | RPP | - | - | -
2 | RPPBA610 | RPP | RPPBA513 | RPPBA413, RPPBA313, RPPBA133, RPPBA213, RPPBA233, TRNBA410 | -
2 | MBCBA110 | MBC | RPPBA533 | RPPBA433, RPPBA333, RPPBA233, RPPBA154 | -
2 | UDPBA310 | UDP | MBCBA110 | RPPBA333, RPPBA433, RPPBA533, RPPBA154, RPPBA254, RPPBA354, RPPBA454, RPPBA554 | 2500A, 480V, 3, , 3W, 65kAIC
2 | BSWBZ210 | BSW | - | - | -
2 | BSWBZ310 | BSW | - | - | -
2 | BSWBZ210 | BSW | - | - | -
2 | BSWBZ310 | BSW | - | - | -
2 | ATSBA130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
2 | ATSBA230 | ATS | - | - | 800A,480V, 3, , 3-POLE
2 | ATSBA330 | ATS | BSWBZ310 | BSWBZ310 | 800A,480V, 3, , 3-POLE
2 | ATSBA430 | ATS | - | - | -
2 | PDUBA210 | PDU | ATSBA130 | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | PDUBA420 | PDU | ATSBA230 | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | PDUBA630 | PDU | ATSBA330 | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | PDUBA840 | PDU | ATSBA430 | - | 500KVA, K4 RATING, 480V:415Y/240V
2 | RPPBA123 | RPP | - | - | -
2 | RPPBA223 | RPP | - | - | -
2 | RPPBA323 | RPP | - | - | -
2 | RPPBA423 | RPP | - | - | -
2 | RPPBA523 | RPP | - | - | -
2 | RPPBA143 | RPP | - | - | -
2 | RPPBA243 | RPP | - | - | -
2 | RPPBA343 | RPP | - | - | -
2 | RPPBA443 | RPP | - | - | -
2 | RPPBA543 | RPP | - | - | -
2 | RPPBA164 | RPP | - | - | -
2 | RPPBA264 | RPP | - | - | -
2 | RPPBA364 | RPP | - | - | -
2 | RPPBA464 | RPP | - | - | -
2 | RPPBA564 | RPP | - | - | -
2 | RPPBA184 | RPP | - | - | -
2 | RPPBA284 | RPP | - | - | -
2 | RPPBA384 | RPP | - | - | -
2 | RPPBA484 | RPP | - | - | -
2 | RPPBA584 | RPP | - | - | -
3 | GENBB100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
3 | GSBBB110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
3 | TRNBB110 | TRN | - | - | -
3 | GSBBA110 | GSB | - | - | -
3 | GSBBC110 | GSB | - | - | -
3 | MSBBB110 | MSB | TRNBB110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
3 | MDPBB110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
3 | UPSBB110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
3 | UPSBB210 | UPS | MDPBB110 | - | 1000kVA/1000kW, 480Y/277V, 3
3 | EPPBZ110 | EPP | - | - | -
3 | EPPBZ110 | EPP | - | - | -
3 | EPPBZ110 | EPP | - | - | -
3 | TRNBB310 | TRN | - | - | -
3 | TRNBB410 | TRN | TRNBB310 | - | 480V:480Y/277, 30KVA, NEMA 1
3 | UPBBB110 | UPB | - | - | -
3 | UPBBB210 | UPB | - | - | -
3 | UPBBB310 | UPB | - | - | -
3 | UPBBB410 | UPB | - | - | -
3 | UPBBB510 | UPB | - | - | -
3 | UPBBB120 | UPB | - | - | -
3 | UPBBB220 | UPB | - | - | -
3 | UPBBB320 | UPB | EPPBZ110 | - | -
3 | UPBBB420 | UPB | EPPBZ110 | - | -
3 | UPBBB520 | UPB | EPPBZ110 | - | -
3 | EPPBZ210 | EPP | UPBBB520 | EPPBZ110, EPPBZ110, EPPBZ110 | -
3 | EPPBZ210 | EPP | ELPBB110 | EPPBZ110, EPPBZ110, EPPBZ110 | -
3 | ELPBB110 | ELP | TRNBB310 | TRNBB410, EPPBZ110 | -
3 | EPPBB230 | EPP | ELPBB110 | TRNBB410, TRNBB310 | -
3 | MBCBB110 | MBC | UPBBB110 | UPBBB210 | 2500AF, 2500AT
3 | TRNBB210 | TRN | EPPBB230 | ELPBB110, TRNBB410, TRNBB310 | -
3 | ELPBB240 | ELP | TRNBB210 | EPPBB230, ELPBB110, TRNBB410 | -
3 | EPPBB120 | EPP | TRNBB210 | ELPBB240, EPPBB230 | -
3 | STSBB110 | STS | - | - | -
3 | STSBB210 | STS | - | - | -
4 | MBCBB110 | MBC | - | - | -
4 | MBCBB110 | MBC | - | - | -
4 | BSWBZ110 | BSW | MBCBB110 | - | -
4 | BSWBZ110 | BSW | MBCBB110 | - | -
4 | BSWBZ110 | BSW | - | - | -
4 | STSBB110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
4 | STSBB210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
4 | UDPBB110 | UDP | STSBB110 | - | 1600A, 480V, 3, , 3W, 65kAIC
4 | UDPBB220 | UDP | STSBB210 | - | 1600A, 480V, 3, , 3W, 65kAIC
4 | PDUBB110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
4 | PDUBB310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
4 | PDUBB520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
4 | PDUBB720 | PDU | - | - | 500KVA, K4 RATING
4 | TRNBB550 | TRN | - | - | -
4 | RPPBB113 | RPP | - | - | -
4 | RPPBB213 | RPP | - | - | -
4 | RPPBB313 | RPP | - | - | -
4 | RPPBB413 | RPP | - | - | -
4 | RPPBB513 | RPP | - | - | -
4 | RPPBB133 | RPP | - | - | -
4 | RPPBB233 | RPP | - | - | -
4 | RPPBB333 | RPP | - | - | -
4 | RPPBB433 | RPP | - | - | -
4 | RPPBB533 | RPP | - | - | -
4 | RPPBB154 | RPP | - | - | -
4 | RPPBB254 | RPP | TRNBB550 | - | -
4 | RPPBB354 | RPP | TRNBB550 | - | -
4 | RPPBB454 | RPP | TRNBB550 | - | -
4 | RPPBB554 | RPP | TRNBB550 | - | -
4 | RPPBB174 | RPP | TRNBB550 | - | -
4 | RPPBB274 | RPP | - | - | -
4 | RPPBB374 | RPP | - | - | -
4 | RPPBB474 | RPP | - | - | -
4 | RPPBB574 | RPP | - | - | -
4 | RPPBB650 | RPP | RPPBB554 | RPPBB454, RPPBB354, RPPBB174, RPPBB254, TRNBB550 | -
4 | MBCBB110 | MBC | RPPBB533 | RPPBB433, RPPBB333, RPPBB233, RPPBB154 | -
4 | UDPBB310 | UDP | MBCBB110 | RPPBB333, RPPBB433, RPPBB533, RPPBB154, RPPBB254, RPPBB354, RPPBB454, RPPBB554 | 2500A, 480V, 3, , 3W, 65kAIC
4 | BSWBZ210 | BSW | - | - | -
4 | BSWBZ310 | BSW | - | - | -
4 | BSWBZ210 | BSW | - | - | -
4 | BSWBZ210 | BSW | - | - | -
4 | BSWBZ310 | BSW | BSWBZ210 | - | -
4 | ATSBB130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
4 | ATSBB230 | ATS | - | - | 800A,480V, 3, , 3-POLE
4 | ATSBB330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
4 | ATSBB430 | ATS | - | - | -
4 | PDUBB210 | PDU | ATSBB130 | - | 500KVA, K4 RATING, 480V:415Y/240V
4 | PDUBB420 | PDU | ATSBB230 | - | 500KVA, K4 RATING, 480V:415Y/240V
4 | PDUBB630 | PDU | ATSBB330 | - | 500KVA, K4 RATING, 480V:415Y/240V
4 | PDUBB840 | PDU | ATSBB430 | - | 500KVA, K4 RATING, 480V:415Y/240V
4 | RPPBB123 | RPP | - | - | -
4 | RPPBB223 | RPP | - | - | -
4 | RPPBB323 | RPP | - | - | -
4 | RPPBB423 | RPP | - | - | -
4 | RPPBB523 | RPP | - | - | -
4 | RPPBB143 | RPP | - | - | -
4 | RPPBB243 | RPP | - | - | -
4 | RPPBB343 | RPP | - | - | -
4 | RPPBB443 | RPP | - | - | -
4 | RPPBB543 | RPP | - | - | -
4 | RPPBB164 | RPP | - | - | -
4 | RPPBB264 | RPP | - | - | -
4 | RPPBB364 | RPP | - | - | -
4 | RPPBB464 | RPP | - | - | -
4 | RPPBB564 | RPP | - | - | -
4 | RPPBB184 | RPP | - | - | -
4 | RPPBB284 | RPP | - | - | -
4 | RPPBB384 | RPP | - | - | -
4 | RPPBB484 | RPP | - | - | -
4 | RPPBB584 | RPP | - | - | -
5 | GENBC100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
5 | GSBBC110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
5 | TRNBC110 | TRN | - | - | -
5 | GSBBB110 | GSB | - | - | -
5 | GSBBZ110 | GSB | - | - | -
5 | MSBBC110 | MSB | TRNBC110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
5 | MDPBC110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
5 | UPSBC110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
5 | UPSBC210 | UPS | MDPBC110 | - | 1000kVA/1000kW, 480Y/277V, 3
5 | EPPBZ110 | EPP | - | - | -
5 | EPPBZ110 | EPP | - | - | -
5 | EPPBZ110 | EPP | - | - | -
5 | TRNBC310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
5 | UPBBC110 | UPB | - | - | -
5 | UPBBC210 | UPB | - | - | -
5 | UPBBC310 | UPB | - | - | -
5 | UPBBC410 | UPB | - | - | -
5 | UPBBC510 | UPB | - | - | -
5 | UPBBC120 | UPB | - | - | -
5 | UPBBC220 | UPB | - | - | -
5 | UPBBC320 | UPB | EPPBZ110 | - | -
5 | UPBBC420 | UPB | EPPBZ110 | - | -
5 | UPBBC520 | UPB | EPPBZ110 | - | -
5 | EPPBZ210 | EPP | UPBBC520 | EPPBZ110, EPPBZ110, EPPBZ110 | -
5 | EPPBZ210 | EPP | EPPBZ110 | EPPBZ110, EPPBZ110 | -
5 | EPPBZ210 | EPP | ELPBC110 | EPPBZ110, EPPBZ110, EPPBZ110 | -
5 | ELPBC110 | ELP | TRNBC310 | EPPBZ110 | -
5 | MBCBC110 | MBC | UPBBC110 | UPBBC210 | 2500AF, 2500AT
5 | TRNBC210 | TRN | ELPBC110 | EPPBZ210, TRNBC310 | -
5 | ELPBC230 | ELP | TRNBC210 | ELPBC110, TRNBC310 | -
5 | EPPBC120 | EPP | TRNBC210 | ELPBC230 | -
5 | STSBC110 | STS | - | - | -
5 | STSBC210 | STS | - | - | -
6 | MBCBC110 | MBC | - | - | -
6 | MBCBC110 | MBC | - | - | -
6 | BSWBZ110 | BSW | MBCBC110 | - | -
6 | BSWBZ110 | BSW | MBCBC110 | - | -
6 | BSWBZ110 | BSW | - | - | -
6 | STSBC110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
6 | STSBC210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
6 | UDPBC110 | UDP | STSBC110 | - | 1600A, 480V, 3, , 3W, 65kAIC
6 | UDPBC220 | UDP | STSBC210 | - | 1600A, 480V, 3, , 3W, 65kAIC
6 | PDUBC110 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
6 | PDUBC310 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
6 | PDUBC520 | PDU | - | - | 500KVA, 480V:415Y/240V
6 | PDUBC720 | PDU | - | - | 500KVA
6 | RPPBC113 | RPP | - | - | -
6 | RPPBC213 | RPP | - | - | -
6 | RPPBC313 | RPP | - | - | -
6 | RPPBC413 | RPP | - | - | -
6 | RPPBC513 | RPP | - | - | -
6 | RPPBC133 | RPP | - | - | -
6 | RPPBC233 | RPP | - | - | -
6 | RPPBC333 | RPP | - | - | -
6 | RPPBC433 | RPP | - | - | -
6 | RPPBC533 | RPP | - | - | -
6 | RPPBC154 | RPP | - | - | -
6 | RPPBC254 | RPP | - | - | -
6 | RPPBC354 | RPP | - | - | -
6 | RPPBC454 | RPP | - | - | -
6 | RPPBC554 | RPP | - | - | -
6 | RPPBC174 | RPP | - | - | -
6 | RPPBC274 | RPP | - | - | -
6 | RPPBC374 | RPP | - | - | -
6 | RPPBC474 | RPP | - | - | -
6 | RPPBC574 | RPP | - | - | -
6 | MBCBC110 | MBC | RPPBC533 | RPPBC433, RPPBC333, RPPBC233, RPPBC154 | -
6 | UDPBC310 | UDP | MBCBC110 | RPPBC333, RPPBC433, RPPBC533, RPPBC154, RPPBC254, RPPBC354, RPPBC454, RPPBC554 | 2500A, 480V, 3, , 3W, 65kAIC
6 | BSWBZ210 | BSW | - | - | -
6 | BSWBZ310 | BSW | - | - | -
6 | BSWBZ210 | BSW | - | - | -
6 | BSWBZ210 | BSW | - | - | -
6 | BSWBZ310 | BSW | - | - | -
6 | ATSBC130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
6 | ATSBC230 | ATS | - | - | 800A,480V, 3, , 3-POLE
6 | ATSBC330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
6 | ATSBC430 | ATS | - | - | -
6 | PDUBC210 | PDU | ATSBC130 | - | 500KVA, 480V:415Y/240V
6 | PDUBC420 | PDU | ATSBC230 | - | 500KVA, 480V:415Y/240V
6 | PDUBC630 | PDU | ATSBC330 | - | 500KVA, 480V:415Y/240V
6 | PDUBC840 | PDU | ATSBC430 | - | 500KVA, 480V:415Y/240V
6 | RPPBC123 | RPP | - | - | -
6 | RPPBC223 | RPP | - | - | -
6 | RPPBC323 | RPP | - | - | -
6 | RPPBC423 | RPP | - | - | -
6 | RPPBC523 | RPP | - | - | -
6 | RPPBC143 | RPP | - | - | -
6 | RPPBC243 | RPP | - | - | -
6 | RPPBC343 | RPP | - | - | -
6 | RPPBC443 | RPP | - | - | -
6 | RPPBC543 | RPP | - | - | -
6 | RPPBC164 | RPP | - | - | -
6 | RPPBC264 | RPP | - | - | -
6 | RPPBC364 | RPP | - | - | -
6 | RPPBC464 | RPP | - | - | -
6 | RPPBC564 | RPP | - | - | -
6 | RPPBC184 | RPP | - | - | -
6 | RPPBC284 | RPP | - | - | -
6 | RPPBC384 | RPP | - | - | -
6 | RPPBC484 | RPP | - | - | -
6 | RPPBC584 | RPP | - | - | -
7 | GENBD100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
7 | GSBBD110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
7 | TRNBD110 | TRN | - | - | -
7 | GSBBZ110 | GSB | - | - | -
7 | GSBBE110 | GSB | - | - | -
7 | MSBBD110 | MSB | TRNBD110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
7 | MDPBD110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
7 | UPSBD110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
7 | UPSBD210 | UPS | MDPBD110 | - | 1000kVA/1000kW, 480Y/277V, 3
7 | EPPBZ110 | EPP | - | - | -
7 | EPPBZ110 | EPP | - | - | -
7 | EPPBZ110 | EPP | - | - | -
7 | TRNBD310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
7 | UPBBD110 | UPB | - | - | -
7 | UPBBD210 | UPB | - | - | -
7 | UPBBD310 | UPB | - | - | -
7 | UPBBD410 | UPB | - | - | -
7 | UPBBD510 | UPB | - | - | -
7 | UPBBD120 | UPB | - | - | -
7 | UPBBD220 | UPB | - | - | -
7 | UPBBD320 | UPB | EPPBZ110 | - | -
7 | UPBBD420 | UPB | EPPBZ110 | - | -
7 | UPBBD520 | UPB | EPPBZ110 | - | -
7 | EPPBZ210 | EPP | UPBBD520 | EPPBZ110, EPPBZ110, EPPBZ110 | -
7 | EPPBZ210 | EPP | EPPBZ110 | EPPBZ110, EPPBZ110 | -
7 | EPPBZ210 | EPP | ELPBD110 | EPPBZ110, EPPBZ110, EPPBZ110 | -
7 | ELPBD110 | ELP | TRNBD310 | EPPBZ110 | -
7 | MBCBD110 | MBC | UPBBD110 | UPBBD210 | 2500AF, 2500AT
7 | TRNBD210 | TRN | ELPBD110 | EPPBZ210, TRNBD310 | -
7 | ELPBD230 | ELP | TRNBD210 | ELPBD110, TRNBD310 | -
7 | EPPBD120 | EPP | TRNBD210 | ELPBD230 | -
7 | STSBD110 | STS | - | - | -
7 | STSBD210 | STS | - | - | -
8 | MBCBD110 | MBC | - | - | -
8 | MBCBD110 | MBC | - | - | -
8 | BSWBZ110 | BSW | MBCBD110 | - | -
8 | BSWBZ110 | BSW | MBCBD110 | - | -
8 | BSWBZ110 | BSW | - | - | -
8 | STSBD110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
8 | STSBD210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
8 | UDPBD110 | UDP | STSBD110 | - | 1600A, 480V, 3, , 3W, 65kAIC
8 | UDPBD220 | UDP | STSBD210 | - | 1600A, 480V, 3, , 3W, 65kAIC
8 | PDUBD110 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
8 | PDUBD310 | PDU | - | - | 500KVA, 480V:415Y/240V, 65kAIC
8 | PDUBD520 | PDU | - | - | 500KVA, 480V:415Y/240V
8 | PDUBD720 | PDU | - | - | 500KVA
8 | RPPBD113 | RPP | - | - | -
8 | RPPBD213 | RPP | - | - | -
8 | RPPBD313 | RPP | - | - | -
8 | RPPBD413 | RPP | - | - | -
8 | RPPBD513 | RPP | - | - | -
8 | RPPBD133 | RPP | - | - | -
8 | RPPBD233 | RPP | - | - | -
8 | RPPBD333 | RPP | - | - | -
8 | RPPBD433 | RPP | - | - | -
8 | RPPBD533 | RPP | - | - | -
8 | RPPBD154 | RPP | - | - | -
8 | RPPBD254 | RPP | - | - | -
8 | RPPBD354 | RPP | - | - | -
8 | RPPBD454 | RPP | - | - | -
8 | RPPBD554 | RPP | - | - | -
8 | RPPBD174 | RPP | - | - | -
8 | RPPBD274 | RPP | - | - | -
8 | RPPBD374 | RPP | - | - | -
8 | RPPBD474 | RPP | - | - | -
8 | RPPBD574 | RPP | - | - | -
8 | MBCBD110 | MBC | RPPBD533 | RPPBD433, RPPBD333, RPPBD233, RPPBD154 | -
8 | UDPBD310 | UDP | MBCBD110 | RPPBD333, RPPBD433, RPPBD533, RPPBD154, RPPBD254, RPPBD354, RPPBD454, RPPBD554 | 2500A, 480V, 3, , 3W, 65kAIC
8 | BSWBZ210 | BSW | - | - | -
8 | BSWBZ310 | BSW | - | - | -
8 | BSWBZ210 | BSW | - | - | -
8 | BSWBZ210 | BSW | - | - | -
8 | BSWBZ310 | BSW | - | - | -
8 | ATSBD130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
8 | ATSBD230 | ATS | - | - | 800A,480V, 3, , 3-POLE
8 | ATSBD330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
8 | ATSBD430 | ATS | - | - | -
8 | PDUBD210 | PDU | ATSBD130 | - | 500KVA, 480V:415Y/240V
8 | PDUBD420 | PDU | ATSBD230 | - | 500KVA, 480V:415Y/240V
8 | PDUBD630 | PDU | ATSBD330 | - | 500KVA, 480V:415Y/240V
8 | PDUBD840 | PDU | ATSBD430 | - | 500KVA, 480V:415Y/240V
8 | RPPBD123 | RPP | - | - | -
8 | RPPBD223 | RPP | - | - | -
8 | RPPBD323 | RPP | - | - | -
8 | RPPBD423 | RPP | - | - | -
8 | RPPBD523 | RPP | - | - | -
8 | RPPBD143 | RPP | - | - | -
8 | RPPBD243 | RPP | - | - | -
8 | RPPBD343 | RPP | - | - | -
8 | RPPBD443 | RPP | - | - | -
8 | RPPBD543 | RPP | - | - | -
8 | RPPBD164 | RPP | - | - | -
8 | RPPBD264 | RPP | - | - | -
8 | RPPBD364 | RPP | - | - | -
8 | RPPBD464 | RPP | - | - | -
8 | RPPBD564 | RPP | - | - | -
8 | RPPBD184 | RPP | - | - | -
8 | RPPBD284 | RPP | - | - | -
8 | RPPBD384 | RPP | - | - | -
8 | RPPBD484 | RPP | - | - | -
8 | RPPBD584 | RPP | - | - | -
9 | GENBE100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
9 | GSBBE110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
9 | TRNBE110 | TRN | - | - | -
9 | GSBBD110 | GSB | - | - | -
9 | GSBBF110 | GSB | - | - | -
9 | MSBBE110 | MSB | TRNBE110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
9 | MDPBE110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
9 | UPSBE110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
9 | UPSBE210 | UPS | MDPBE110 | - | 1000kVA/1000kW, 480Y/277V, 3
9 | EPPBZ110 | EPP | - | - | -
9 | EPPBZ110 | EPP | - | - | -
9 | TRNBE310 | TRN | - | - | 480V:480Y/277, 30KVA, NEMA 1
9 | UPBBE110 | UPB | - | - | -
9 | UPBBE210 | UPB | - | - | -
9 | UPBBE310 | UPB | - | - | -
9 | UPBBE410 | UPB | - | - | -
9 | UPBBE510 | UPB | - | - | -
9 | UPBBE120 | UPB | - | - | -
9 | UPBBE220 | UPB | - | - | -
9 | UPBBE320 | UPB | EPPBZ110 | - | -
9 | UPBBE420 | UPB | EPPBZ110 | - | -
9 | UPBBE520 | UPB | EPPBZ110 | - | -
9 | EPPBZ210 | EPP | UPBBE520 | EPPBZ110, EPPBZ110 | -
9 | EPPBZ210 | EPP | ELPBE110 | EPPBZ110, EPPBZ110 | -
9 | EPPBZ210 | EPP | ELPBE110 | EPPBZ110, EPPBZ110 | -
9 | ELPBE110 | ELP | TRNBE310 | - | -
9 | MBCBE110 | MBC | UPBBE110 | UPBBE210 | 2500AF, 2500AT
9 | TRNBE210 | TRN | ELPBE110 | EPPBZ210, TRNBE310 | -
9 | ELPBE230 | ELP | TRNBE210 | ELPBE110, TRNBE310 | -
9 | EPPBE120 | EPP | TRNBE210 | ELPBE230 | -
9 | STSBE110 | STS | - | - | -
9 | STSBE210 | STS | - | - | -
10 | MBCBE110 | MBC | - | - | -
10 | MBCBE110 | MBC | - | - | -
10 | BSWBZ110 | BSW | MBCBE110 | - | -
10 | BSWBZ110 | BSW | MBCBE110 | - | -
10 | BSWBZ110 | BSW | - | - | -
10 | STSBE110 | STS | BSWBZ110 | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
10 | STSBE210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
10 | UDPBE110 | UDP | STSBE110 | - | 1600A, 480V, 3, , 3W, 65kAIC
10 | UDPBE220 | UDP | STSBE210 | - | 1600A, 480V, 3, , 3W, 65kAIC
10 | PDUBE110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
10 | PDUBE310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
10 | PDUBE520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | PDUBE720 | PDU | - | - | 500KVA, K4 RATING
10 | TRNBE450 | TRN | - | - | -
10 | RPPBE113 | RPP | - | - | -
10 | RPPBE213 | RPP | - | - | -
10 | RPPBE313 | RPP | - | - | -
10 | RPPBE413 | RPP | - | - | -
10 | RPPBE513 | RPP | - | - | -
10 | RPPBE133 | RPP | - | - | -
10 | RPPBE233 | RPP | - | - | -
10 | RPPBE333 | RPP | - | - | -
10 | RPPBE433 | RPP | - | - | -
10 | RPPBE533 | RPP | - | - | -
10 | RPPBE154 | RPP | - | - | -
10 | RPPBE254 | RPP | TRNBE450 | - | -
10 | RPPBE354 | RPP | TRNBE450 | - | -
10 | RPPBE454 | RPP | TRNBE450 | - | -
10 | RPPBE554 | RPP | TRNBE450 | - | -
10 | RPPBE174 | RPP | TRNBE450 | - | -
10 | RPPBE274 | RPP | - | - | -
10 | RPPBE374 | RPP | - | - | -
10 | RPPBE474 | RPP | - | - | -
10 | RPPBE574 | RPP | - | - | -
10 | RPPBE650 | RPP | RPPBE554 | RPPBE454, RPPBE354, RPPBE174, RPPBE254, TRNBE450 | -
10 | MBCBE110 | MBC | RPPBE533 | RPPBE433, RPPBE333, RPPBE233, RPPBE154 | -
10 | UDPBE310 | UDP | MBCBE110 | RPPBE333, RPPBE433, RPPBE533, RPPBE154, RPPBE254, RPPBE354, RPPBE454, RPPBE554 | 2500A, 480V, 3, , 3W, 65kAIC
10 | RPPBE760 | RPP | RPPBE650 | - | -
10 | BSWBZ210 | BSW | - | - | -
10 | BSWBZ310 | BSW | - | - | -
10 | BSWBZ210 | BSW | - | - | -
10 | BSWBZ210 | BSW | - | - | -
10 | BSWBZ310 | BSW | - | - | -
10 | ATSBE130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
10 | ATSBE230 | ATS | - | - | 800A,480V, 3, , 3-POLE
10 | ATSBE330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
10 | ATSBE430 | ATS | - | - | -
10 | PDUBE210 | PDU | ATSBE130 | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | PDUBE420 | PDU | ATSBE230 | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | PDUBE630 | PDU | ATSBE330 | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | PDUBE840 | PDU | ATSBE430 | - | 500KVA, K4 RATING, 480V:415Y/240V
10 | RPPBE123 | RPP | - | - | -
10 | RPPBE223 | RPP | - | - | -
10 | RPPBE323 | RPP | - | - | -
10 | RPPBE423 | RPP | - | - | -
10 | RPPBE523 | RPP | - | - | -
10 | RPPBE143 | RPP | - | - | -
10 | RPPBE243 | RPP | - | - | -
10 | RPPBE343 | RPP | - | - | -
10 | RPPBE443 | RPP | - | - | -
10 | RPPBE543 | RPP | - | - | -
10 | RPPBE164 | RPP | - | - | -
10 | RPPBE264 | RPP | - | - | -
10 | RPPBE364 | RPP | - | - | -
10 | RPPBE464 | RPP | - | - | -
10 | RPPBE564 | RPP | - | - | -
10 | RPPBE184 | RPP | - | - | -
10 | RPPBE284 | RPP | - | - | -
10 | RPPBE384 | RPP | - | - | -
10 | RPPBE484 | RPP | - | - | -
10 | RPPBE584 | RPP | - | - | -
11 | GENBF100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
11 | GSBBF110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
11 | TRNBF110 | TRN | - | - | -
11 | GSBBE110 | GSB | - | - | -
11 | MSBBF110 | MSB | TRNBF110 | - | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
11 | MDPBF110 | MDP | - | - | 600A, 480Y/277V, 3, , 3W, 65kAIC
11 | UPSBF110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
11 | UPSBF210 | UPS | MDPBF110 | - | 1000kVA/1000kW, 480Y/277V, 3
11 | EPPBZ110 | EPP | - | - | -
11 | EPPBZ110 | EPP | - | - | -
11 | TRNBF310 | TRN | - | - | -
11 | UPBBF110 | UPB | - | - | -
11 | UPBBF210 | UPB | - | - | -
11 | UPBBF310 | UPB | - | - | -
11 | UPBBF410 | UPB | - | - | -
11 | UPBBF510 | UPB | - | - | -
11 | UPBBF120 | UPB | - | - | -
11 | UPBBF220 | UPB | - | - | -
11 | UPBBF320 | UPB | EPPBZ110 | - | -
11 | UPBBF420 | UPB | EPPBZ110 | - | -
11 | UPBBF520 | UPB | EPPBZ110 | - | -
11 | EPPBZ210 | EPP | UPBBF520 | EPPBZ110, EPPBZ110 | -
11 | EPPBZ210 | EPP | ELPBF110 | EPPBZ110, EPPBZ110 | -
11 | EPPBZ210 | EPP | ELPBF110 | EPPBZ110, EPPBZ110 | -
11 | ELPBF110 | ELP | TRNBF310 | - | -
11 | MBCBF110 | MBC | UPBBF110 | UPBBF210 | 2500AF, 2500AT
11 | TRNBF210 | TRN | EPPBF230 | EPPBZ210, ELPBF110, TRNBF310 | -
11 | EPPBF230 | EPP | ELPBF110 | TRNBF310 | -
11 | EPPBF120 | EPP | TRNBF210 | EPPBF230 | -
11 | EPPBF320 | EPP | EPPBF230 | TRNBF210 | -
11 | STSBF110 | STS | - | - | -
11 | STSBF210 | STS | - | - | -
12 | MBCBF110 | MBC | - | - | -
12 | MBCBF110 | MBC | - | - | -
12 | BSWBZ110 | BSW | MBCBF110 | - | -
12 | BSWBZ110 | BSW | - | - | -
12 | STSBF110 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
12 | STSBF210 | STS | - | - | 1600A, 480V, 3, , 3W, 3 POLE, 65kAIC
12 | UDPBF110 | UDP | STSBF110 | - | 1600A, 480V, 3, , 3W, 65kAIC
12 | UDPBF220 | UDP | STSBF210 | - | 1600A, 480V, 3, , 3W, 65kAIC
12 | PDUBF110 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
12 | PDUBF310 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC
12 | PDUBF520 | PDU | - | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | PDUBF720 | PDU | - | - | 500KVA, K4 RATING
12 | TRNBF410 | TRN | - | - | -
12 | RPPBF113 | RPP | - | - | -
12 | RPPBF213 | RPP | TRNBF410 | - | -
12 | RPPBF313 | RPP | TRNBF410 | - | -
12 | RPPBF413 | RPP | TRNBF410 | - | -
12 | RPPBF513 | RPP | TRNBF410 | - | -
12 | RPPBF133 | RPP | TRNBF410 | - | -
12 | RPPBF233 | RPP | TRNBF410 | - | -
12 | RPPBF333 | RPP | - | - | -
12 | RPPBF433 | RPP | - | - | -
12 | RPPBF533 | RPP | - | - | -
12 | RPPBF154 | RPP | - | - | -
12 | RPPBF254 | RPP | - | - | -
12 | RPPBF354 | RPP | - | - | -
12 | RPPBF454 | RPP | - | - | -
12 | RPPBF554 | RPP | - | - | -
12 | RPPBF174 | RPP | - | - | -
12 | RPPBF274 | RPP | - | - | -
12 | RPPBF374 | RPP | - | - | -
12 | RPPBF474 | RPP | - | - | -
12 | RPPBF574 | RPP | - | - | -
12 | RPPBF610 | RPP | RPPBF513 | RPPBF413, RPPBF313, RPPBF133, RPPBF213, RPPBF233, TRNBF410 | -
12 | MBCBF110 | MBC | RPPBF533 | RPPBF433, RPPBF333, RPPBF233, RPPBF154 | -
12 | UDPBF310 | UDP | MBCBF110 | RPPBF333, RPPBF433, RPPBF533, RPPBF154, RPPBF254, RPPBF354, RPPBF454, RPPBF554 | 2500A, 480V, 3, , 3W, 65kAIC
12 | RPPBF760 | RPP | RPPBF610 | - | -
12 | BSWBZ210 | BSW | - | - | -
12 | BSWBZ310 | BSW | - | - | -
12 | BSWBZ210 | BSW | - | - | -
12 | BSWBZ210 | BSW | - | - | -
12 | BSWBZ310 | BSW | - | - | -
12 | ATSBF130 | ATS | BSWBZ210 | BSWBZ210 | 800A,480V, 3, , 3-POLE
12 | ATSBF230 | ATS | - | - | 800A,480V, 3, , 3-POLE
12 | ATSBF330 | ATS | BSWBZ310 | BSWBZ210, BSWBZ310 | 800A,480V, 3, , 3-POLE
12 | ATSBF430 | ATS | - | - | -
12 | PDUBF210 | PDU | ATSBF130 | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | PDUBF420 | PDU | ATSBF230 | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | PDUBF630 | PDU | ATSBF330 | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | PDUBF840 | PDU | ATSBF430 | - | 500KVA, K4 RATING, 480V:415Y/240V
12 | RPPBF123 | RPP | - | - | -
12 | RPPBF223 | RPP | - | - | -
12 | RPPBF323 | RPP | - | - | -
12 | RPPBF423 | RPP | - | - | -
12 | RPPBF523 | RPP | - | - | -
12 | RPPBF143 | RPP | - | - | -
12 | RPPBF243 | RPP | - | - | -
12 | RPPBF343 | RPP | - | - | -
12 | RPPBF443 | RPP | - | - | -
12 | RPPBF543 | RPP | - | - | -
12 | RPPBF164 | RPP | - | - | -
12 | RPPBF264 | RPP | - | - | -
12 | RPPBF364 | RPP | - | - | -
12 | RPPBF464 | RPP | - | - | -
12 | RPPBF564 | RPP | - | - | -
12 | RPPBF184 | RPP | - | - | -
12 | RPPBF284 | RPP | - | - | -
12 | RPPBF384 | RPP | - | - | -
12 | RPPBF484 | RPP | - | - | -
12 | RPPBF584 | RPP | - | - | -
13 | GENBH100 | GEN | - | - | 1750kW/2187.5KVA, 480Y/277V, 3P, 4W, 0.80PF
13 | TRNBH110 | TRN | - | - | -
13 | ATSBH110 | ATS | TRNBH110 | - | 2500AF, 2500A, 480V, 3, , 4W, 4-POLE, 2500AT, 65kAIC, SE RATED, OPEN/DELAYED, 100%, LSIG, ERMS
13 | MSBBH110 | MSB | - | - | 2500A, 480Y/277V, 3, , 4W, 65kAIC
13 | TRNBH310 | TRN | - | - | 480V:208Y/120, PANEL, 75KVA, NEMA 1
13 | TRNBH510 | TRN | - | - | 480V:208Y/120, PANEL, 75KVA, NEMA 1
13 | TRNBH710 | TRN | - | - | 480V:208Y/120, PANEL
13 | TRNBH910 | TRN | - | - | 480V:208Y/120
13 | ELPBH110 | ELP | TRNBH310 | - | -
13 | ELPBH210 | ELP | TRNBH310 | TRNBH510 | -
13 | ELPBH410 | ELP | TRNBH310 | TRNBH510 | -
13 | ELPBH510 | ELP | TRNBH510 | TRNBH710 | -
13 | ELPBH710 | ELP | TRNBH510 | TRNBH710 | -
13 | ELPBH810 | ELP | TRNBH710 | TRNBH910 | -
13 | EPPBH230 | EPP | ELPBH110 | ELPBH210, ELPBH410, TRNBH310 | -
13 | EPPBH550 | EPP | ELPBH410 | ELPBH510, ELPBH210, ELPBH710, TRNBH310, TRNBH510 | -
13 | EPPBH770 | EPP | ELPBH710 | ELPBH810, ELPBH510, TRNBH510, TRNBH710 | -
13 | TRNBH210 | TRN | EPPBH230 | ELPBH110, ELPBH210, ELPBH410, TRNBH310 | 480V:208Y/120, 75KVA, NEMA 1
13 | TRNBH440 | TRN | EPPBH550 | EPPBH230, ELPBH210, ELPBH410, ELPBH510, ELPBH710, TRNBH310, TRNBH510 | 480V:208Y/120, 75KVA, NEMA 1
13 | TRNBH670 | TRN | EPPBH770 | EPPBH550, ELPBH510, ELPBH710, ELPBH810, TRNBH510, TRNBH710 | 480V:208Y/120, 75KVA, NEMA 1
13 | ELPBH320 | ELP | EPPBH230 | TRNBH440, TRNBH210, EPPBH550 | -
13 | ELPBH650 | ELP | EPPBH550 | TRNBH670, TRNBH440, EPPBH770 | -
13 | ELPBH980 | ELP | EPPBH770 | TRNBH670 | -
13 | EPPBH120 | EPP | ELPBH320 | TRNBH210, EPPBH230 | -
13 | EPPBH320 | EPP | ELPBH320 | TRNBH210, TRNBH440, EPPBH230, EPPBH550 | -
13 | EPPBH440 | EPP | ELPBH320 | ELPBH650, TRNBH210, TRNBH440, EPPBH230, EPPBH550 | -
13 | EPPBH660 | EPP | ELPBH650 | ELPBH980, TRNBH440, TRNBH670, EPPBH550, EPPBH770 | -
13 | EPPBH870 | EPP | ELPBH980 | ELPBH650, TRNBH670, EPPBH770 | -
13 | EPPBH980 | EPP | ELPBH980 | TRNBH670, EPPBH770 | -
13 | MSBBH110 | MSB | EPPBH660 | EPPBH870, EPPBH980, ELPBH650, ELPBH980 | -
13 | MSBAH110 | MSB | - | - | (ROOF)
13 | UPSBH110 | UPS | - | - | BIB 150A LSI, 80kVA/80kW, N.C. (2) AUX, RECTIFIER, 480V, 3, 208Y/120V, 3, , 3W, INPUT
13 | UPPBH110 | UPP | - | - | -
14 | GENBZ100 | GEN | - | - | 3000kW/3750KVA, 480Y/277V, 3, , 4W, 0.80PF
14 | GSBBZ110 | GSB | - | - | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%
14 | TRNBZ110 | TRN | - | - | -
14 | GSBBC110 | GSB | GSBBD110 | - | -
14 | GSBBD110 | GSB | - | - | -
14 | MSBBZ110 | MSB | TRNBZ110 | - | 4000A, 480Y/277V, 3, , 4W, 100kAIC, S.E. RATED, WOODWARD PLC BREAKER TRANSFER CONTROLLER, BREAKER TRANSFER IS DELAYED OPEN TRANSITION
14 | MDPBZ110 | MDP | - | - | 600A, 480V, 3, , 3W, 65kAIC
14 | ELPBZ110 | ELP | - | - | -
14 | UPSBZ110 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3, , 3W, INPUT, , 3W, OUTPUT
14 | UPSBZ210 | UPS | - | - | 1000kVA/1000kW, 480Y/277V, 3
14 | TRNBZ210 | TRN | ELPBZ110 | - | 480V:208Y/120, 45KVA, NEMA 1
14 | EPPBZ120 | EPP | TRNBZ210 | - | -
14 | EPPBZ210 | EPP | EPPBZ120 | - | 150A, 480V, 3, , 3W, 35kAIC
14 | UPBBZ110 | UPB | - | - | -
14 | UPBBZ210 | UPB | - | - | -
14 | UPBBZ310 | UPB | - | - | -
14 | UPBBZ410 | UPB | - | - | -
14 | UPBBZ510 | UPB | - | - | -
14 | UPBBZ120 | UPB | - | - | -
14 | UPBBZ220 | UPB | - | - | -
14 | UPBBZ320 | UPB | - | - | -
14 | UPBBZ420 | UPB | - | - | -
14 | UPBBZ520 | UPB | - | - | -
14 | MBCBZ110 | MBC | UPBBZ110 | UPBBZ210 | 2500AF, 2500AT, 2500A, 480V, 3, , 3W, 100kAIC, 100%
14 | EPPBZ110 | EPP | - | - | 150A, 480V, 3, , 3W, 35kAIC
14 | BSWBZ110 | BSW | - | - | -
14 | BSWBZ110 | BSW | - | - | -
14 | BSWBZ110 | BSW | - | - | -
14 | BSWBZ210 | BSW | BSWBZ110 | BSWBZ110, BSWBZ110 | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE
14 | BSWBZ210 | BSW | BSWBZ110 | BSWBZ110 | -
14 | BSWBZ310 | BSW | BSWBZ210 | BSWBZ210, BSWBZ110, BSWBZ110, BSWBZ110 | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE
14 | BSWBZ310 | BSW | BSWBZ210 | BSWBZ210, BSWBZ110 | -